FSR on Expansion and Modernization of the MOIN Refinery Project

6

Instrumentation and Control Systems

6.1 Scope and Base of Study

6.1.1

Scope of Study

Scope of the FSR is PetroChina-Costa Rica MOIN Refinery Revamp and Expansion

Project.

Grass root units in the FSR mainly include:

Atmospheric and Vacuum Distillation Unit, Naphtha Hydrotreating Unit, Continuous

Catalytic Reforming Unit, Delayed Coking Unit, Diesel Hydrofining Unit, VGO

Hydrogenation Unit, H

Production Unit, Sulfur Recovery Unit, Isomerization Unit and Dry

2

Gas / LPG treatment Unit.

New utility and auxiliary units in the Project mainly include:

Logistics system, steam system, flare system, water supply and drainage system, power

supply and distribution system, and air separation and compression system.

Instruments and automatic systems mainly include field instruments, control systems and

safe instrumented (emergency shut down) systems for new production units, logistics system,

steam system, waste water treatment system, water supply and drainage system, power supply

and distribution system, and air separation and compression system.

6.1.2

Base of Study

(1)

Information from field investigation

(2)

Design conditions and design requirements for all units.

(3)

Correspondence and minutes of meetings during feasibility study.

6.2 Status of existing Plant Wide Automatic Controls

Existing units in the Project include an Atmospheric and Vacuum Distillation Unit, an

Kerosene Hydrofining Unit, a Reforming Unit, a Visbreaking Unit, a Light Ends Recovery

Unit as well as supporting water supply and drainage system, waste water treatment plant, air

compression station, and steam system.

The Project consists of the following existing systems:

(1)

Existing DCS

Existing DCS

System model: Honeywell TDC3000

Location of installation: Existing CCR

6-1

FSR on Expansion and Modernization of the MOIN Refinery Project

Time of startup: 1967.

Modifications to be conducted: RECOPE is going to revamp the system within 4 years,

solution to which is implementing.

(2)

Existing SIS

Existing SIS control system

Location of installation: Existing CCR

(3)

Conditions of existing instruments:

Pressure, flow and level gauges: Under revamping by RECOPE

Metering gauges for crudes and oil from units: Under revamping by RECOPE

Control valves: Under revamping by RECOPE

6.3 Selection of Plant Wide Control Systems and Instruments

6.3.1

General

Because it is required to revamp the existing units without production halts, design

principle for automatic engineering is to incorporate control system configuration plan to

install a new control system in a new building without any influence on existing production

according to the construction plan of the grassroot unit.

The new control system is furnished with communication interfaces linking up with the

existing control system, to complete monitoring and alarm displays of existing control system.

For each productin unit, basic automatic process control will be conducted via DCS.

The control systems in the center control room shall be furnished with communication

interfaces linking up with the Plantwide Management Net to provide necessary data and

network structure foundation for Management Information System (MIS).

Plant Wide Control system architecture see the attached drawing 1.

6.3.2

General Level of Plant Wide Controls

(1)

A plant wide CCR with a DCS will be built in the revamping project to achieve

central operation, control and management of new production units, logistics system

and utility systems with level of control reaching advanced level among similar

international plants. Grass root units and supporting production units after expansion

will be equipped with DCS, SIS, CCS, PLC, FAS, and FGDS.

(2)

Control, management and operation of all production units and supporting systems

(unit) in the Project will be integrated. Automatic control of all production units,

logistics system and utilities will reach advanced level of similar plants in the world.

6-2

FSR on Expansion and Modernization of the MOIN Refinery Project

(3)

Process control, monitoring and operation management of all production units,

logistics system and utility facilities will be conducted via DCS in CCR.

All production information for process units, security information is sent through the

network interface OPC to Management Information System to monitor dynamic monitoring

the whole plant.

(4)

For the oil tank farms, install in-line oil prduct quality analyzers, in-line oil product

harmonic control system and in-line harmonic model software, to achieve the

automation of oil to reconcile.

(5)

According to the process requirements and feasibility of the process units, may

consider Atmospheric and Vacuum Distillation Unit, Continuous Catalytic Reforming

Unit adoption and implementation of advanced process control.

(6)

The process plant shall be implemented simultaneously asset management system.

(7)

Being the center and base of plant wide operation, monitoring and control, control

systems of the Project are capable of real time monitoring on complete process from

production, oil logistics, utilities, feed stock and product inflow/outflow to product

quality control.

(8)

The project on the production facilities, production operations and control layer

mainly including:

Distributed Control System (DCS)

Safty Instrumentation System (SIS)

Fire Alarm System (FAS)

Flammable/Toxic Gas Detection System ( FGDS)

Asset Management System( AMS)

Preliminary Analyzer System (PAS)

Advanced Process Control (APC)

Control System for Package (PLC)

Compressor Control System (CCS)

(

)

Management Information System

MIS

(9)

Control and monitoring of logistics tank farms will be conducted via DCS. All data

6-3

FSR on Expansion and Modernization of the MOIN Refinery Project

display, control, logging and alarms for the operation and monitoring of tank farms in

logistics area will be executed in CCR.

(10)

Other integrated automation solutions for process units.

Other integrated automation solutions for process units shall also include:

MCC (to be implemented by electrical discipline)

Closed-circuit Video System (CCTV ).

6.3.3

General Principle of Selection

All instrument equipment or systems applied in the Project shall be advanced in

technology and reliable in performance, applicable for the Project and commercially proven

products widely used in similar units in the world in recent years, and proven to be

dependable products or systems.

(1)

The control systems shall meet both functional requirements and the requirements

for safety, reliability, real time response, maintainability, expandability, and costs.

Operation tested system of proven technology and high performance/price efficiency

and software and hardware easy to use and maintain shall be selected.

(2)

Measurement and control instruments selected shall be advanced in technology,

reliable in operation, safe and durable, superior in dynamic performance, high in

precision, good in reproducibility, easy to operate and maintain, economical, and in

line with monitoring and control requirements.

6.3.4

Selection of Control System

(1)

DCS

DCS is a comprehensive, integrated, configurable and standardized process control

system, selection principle of which is as following:

1)

Technical level: Up to date technology and system developed and improved in recent

years with open and expandable infrastructure and advanced and reliable hardware

shall be applied.

2)

System redundancy: The system shall be equipped with perfect redundant technology,

including equipment redundancy and performance redundancy. Control stations or

controllers, network communication equipment and components at all levels,

mainframe power supply and channel power supply devices, I/O cards in control loops

shall be 1:1 redundant.

3)

System expandability: All I/O channels and slots for I/O cards shall have 15% spares.

6-4

FSR on Expansion and Modernization of the MOIN Refinery Project

In addition, the systems shall have online expandability.

4)

System openness: The systems shall communicate with systems compatible with

ISO/OSI communication standards. It shall be possible to add simple or standard

interfaces to connect with Ethernet.

5)

System reliability: System MTBF and MTTR level shall be advanced.

6)

System maintenance and faults diagnostic: Systems shall be equipped with perfect

software and hardware fault diagnostic and self diagnostic functions and automatically

record fault alarms and prompt maintenance operators to maintain. All cards of the

systems shall be capable of online plug-in/out and changing.

(2)

SIS

In order to ensure safety of all units, critical process equipment and large machineries as

well as operators, a highly reliable safety instrumented system (SIS) shall be equipped to

execute emergency shutdown and safety interlock protection of all units and critical

equipment.

Major technical performance requirements for SIS:

The system shall be of failsafe models based on PLC and of redundant and fault tolerant

structure. Its safety level shall be configured according to the requirements for SIL analysis

for units. It shall be capable of fault self-diagnostic, SOE and communication with DCS.

In order to ensure high reliability of SIS, the following principles shall be considered:

Independent from DCS

Failsafe model (actuation on blackout)

Safety level of system is compatible with that of units.

Logic structure applies connection method of subsystem blocks.

Reasonable redundant configuration for I/O cards and primary field operation elements

Sufficient operator interfaces.

Flexible automatic/semi-automatic operation means.

Sufficient bypass maintenance switches.

Equipped with fault diagnostic technology, millisecond resolution for first event and

alarm printers

Capable of communication with DCS

Strong expandability and capacibility of online plug-in/out and changing of cards.

(3)

FGDS

6-5

FSR on Expansion and Modernization of the MOIN Refinery Project

Sufficient flammable gas and toxic gas detection sensors shall be installed in the unit

areas according to the distribution of leakage sources from units. Data from the sensors shall

be connected with an independent flammable gas and toxic gas detection and alarm system

(FGDS) for comprehensive monitoring on leakage of flammable gas and toxic gas from the

units in CCR.

The system will be configured as a redundant control and monitoring system based on

PES (Programmable Electronics System). FGDS shall be capable of communication with

DCS.

(4)

Other Control Systems

1)

AMS

In order to ensure effective, long term and stable operation of the units, an AMS is

installed.

AMS is mainly to conduct management functions including maintenance, calibration and

fault diagnostic for field instruments and regulating valves in the units.

AMS servers will be installed in CCR and connect with corresponding DCS LAN.

2)

CCS

Compressors will be equipped with their own control system applying MODBUS RTU

protocol to communicate with DCS for load control, process control and interlock protection.

Local display panels of explosion proof and weather proof models are installed for local

monitoring, startup and shutdown debugging, polling, and maintenance.

CCS is redundant and fault tolerant system equipped with application software capable

of SOE. Machinery specific monitoring and control system shall be supplied by machinery

package supplier.

3)

FAS

Manual fire alarm push buttons will be installed in units and along the perimeters of tank

farm according to the properties of units in the plant. The 50,000 m

external floating roof

3

crude tank will be equipped with temperature detecting cable type automatic fire detection

and alarm system. Critical buildings, e.g., area control centers, substations and power

distribution stations and instrument cabinet rooms will be equipped with FAS.    Main fire

alarm control panel will be installed in CCR and auxiliary fire alarm panels will be installed

in fire station of the plant. Local fire alarm display of the FAS will monitor and control all fire

alarm signals and fire fighting interlocks within unit areas.

4)

CCTV

CCTV system of the Project is a safety protection system capable of strict monitoring

6-6

FSR on Expansion and Modernization of the MOIN Refinery Project

and management of all process units of the Project as well as central management in CCR.

5)

Control System for the Package (PLC)

Specific packages must have a proprietary control system, the system should

communicate with the DCS through the interface unit, the DCS to complete monitoring.

6)

PAS

For complex in-line analyzer (such as: Process Gas Chromatograph), the communication

interface with the network to form a separate analysis instrumentation systems for the

analyzer repair, maintenance and management.

7)

APC

By advanced process control methods, solve such process control problems as process

time-varying, strong coupling, nonlinearity and long time delay, improve control quality,

optimize production operations, improve units processing, product quality and product yield,

reduce energy consumption, so as to achieve the facilities' maximum economic efficiency and

obtain satisfactory results.

Advanced Process Control is based on conventional control of DCS, which uses a variety

of DCS hardware and software functions, and in-line analyzers' analysis results to make

process calculation and establish a multi-variable predictive controller to achieve smooth

operation of the production process and the card edge operation and improve the yield of

desired product.

In the project design, the advanced control platform and interface are reserved.

On this project, it is recommended that priority of using Advanced Process Control be

given to: atmospheric and vacuum distillation unit and continuous catalytic reforming unit.

Based on the completion and implementation of advanced process control, further

execute real-time optimal control. Optimization of the whole plant process shall be further

worked on at a later, proper time.

6.3.5

Instrument Selection

Field instruments and control valves shall be applicable to local environment and fluid

conditions. Instruments and their enclosures, instrument tubing and installation materials shall

be resistant to fluid and environment corrosion.

Electricals of instruments shall meet the requirements for explosion proof and protection

grading of the installation location. Field instruments for explosion hazard areas shall be of

intrinsic safety models while some of them may be of explosion proof types according to the

requirements. Protection level shall not be lower than IP65 for outdoor instruments and IP55

for indoor products.

6-7

FSR on Expansion and Modernization of the MOIN Refinery Project

Advanced, reliable, maintenance free or easy to maintain instruments shall be selected.

Instrument models shall be as identical with existing ones as possible to cut down instrument

varieties.

Remote instruments shall be of electric types normally with smart transmitters.

Regulating valves shall select reliable imported products.

Diaphragms shall be used in pressure and differential pressure measurement for viscous,

corrosive and prone to crystallization fluids. Material of diaphragm shall be selected

according to fluid. Under special circumstance, isolation fluid or flush oil may be used.

Transmitters with diagnostic functions are preferred. When necessary, switch type

instruments shall be used.

Calibration instruments: Except for special calibration instruments and maintenance

tools for units, general calibration instruments and devices shall be considered on plant wide

base. Proper addition according to practical needs based on existing equipment shall be made

to meet the needs in repair and maintenance.

6.4 Automatic Control Plan for Process Unit

6.4.1

Main Automatic Control Plan for Process Unit

Automatic control system mainly executes data acquisition, monitoring, control, and

safety interlock protection on processes of all units and implements computer data processing

and production management to facilitate long term, safe, stable and effective operation of

units so as to ensure product quality.

Automatic control system monitors and controls major process parameters of the units

and transmits them to CCR for central display and recording. Normal parameters will be

equipped with monitoring instruments for local display. Critical parameters will be equipped

with acoustic and visual alarms in CCR. Critical units will be equipped with SIS to ensure

safe production, cut down accident rate, avoid personnel and equipment damage, and mitigate

economic loss.

Concentration sensors with alarms in unit control room and CCR will be installed at

locations possible of flammable or toxic gas leakage.

6.4.2

Main Control Plan for Process Units

(1)

2,000KTPA ADU and 1,500KTPA VDU

1)

Description of Control System

The 2,000KTPA ADU and 1,500KTPA VDU constitute a complex with flammable and

explosive fluids requiring rigorous operation safety. Therefore, automatic control system shall

not only have perfect control capabilities but also possess high reliability and high safety for

6-8

FSR on Expansion and Modernization of the MOIN Refinery Project

safe, reliable and long term operation of the units so as to improve reliability of the automatic

control system, ensure safe production, promote operation management level and yield better

economic returns from unit operation. According to the properties of the units and

requirements for safe production, the following systems will be installed:

DCS

SIS

FGDS

AMS

A WRS will be installed to improve staff management.

a)

The unit will be equipped with a DCS to conduct central control and management for

it.

DCS hardware configuration: The feasibility study will not select specific DCS, but

specifies the following requirements for configuration:

-   Operation stations: 5 sets. Each operation station shall be equipped with separate

electronic unit, display and key board.

-  Engineering stations will be used in system configuration and online system

maintenance.

-    Control stations, monitoring stations, safety barrier cabinets, and terminal cabinets

will be separately configured according to the needs of control and monitoring points.

-    Engineering stations, alarm printers and report printers will be configured according

to the needs of plant wide control system.

b)

Separate SIS compatible with safety rating of units will be installed according to the

requirements of design specifications.    System size will be determined according to

actual number of points.    Safety and reliability will be the top priority of SIS, safety

level of which will meet the requirements of that of the unit. Design of SIS will

incorporate system integrity, safety, reliability, automatic and semi-automatic

operation flexibility, and safety and convenience in system maintenance to make a safe

and convenient system so as to ensure safe and long term operation of the unit.

c)

According to the requirements of design specifications, sufficient flammable gas and

toxic gas detection sensors shall be installed according to the distribution of leakage

sources from units. Data from the sensors shall be connected with flammable gas and

toxic gas detection and alarm system (FGDS) of individual units for comprehensive

monitoring on leakage of flammable gas and toxic gas from the units in CCR.

6-9

FSR on Expansion and Modernization of the MOIN Refinery Project

2)

Major control loops of the unit are as following:

- Cascade control of level in primary distiller bottom with crude flow rate through heat

exchanger before desalting

-    Cascade control of ADU top temperature with ADU overhead reflux

-   Outlet temperature control of the heater will be in cascade with furnace chamber

temperature to regulate fuel flow.

-   Oxygen content control and furnace chamber vacuum control will be applied for

ADU to improve heat efficiency of the heater.

3)

Major interlock protection systems of the unit are as following:

-   ADU interlock.

-   VDU interlock.

Size of control points in the unit:

-    DCS detection points about 800 and control loops about 150.

-    SIS detection points about 160 and control loops about 40.

-  FGDS detection points about 40.

(2)

700 KTPA Delayed Coking Unit

1)

Description of the control system

Automatic control of 700KTPA Delayed Coking Unit consists of coking section,

fractionation section and absorption and stabilization section. (Control design for compressor,

HP water pump and hydraulic decoding system will be provided by the suppliers). Feed to the

unit is VGO. Major products include gasoline, diesel, wax oil, coke, LPG, and dry gas. The

unit features in high operation temperature and viscous, flammable, explosive, corrosive, and

toxic process fluids with strict requirements for operation stability, safety, reliability, and

product quality. Therefore, both software and hardware of the automatic control system must

have high reliability, high safety and high tech. According to the properties of the unit and the

requirements for safe production, the following control systems will be installed:

DCS

SIS

CCS

FGDS

AMS

A WRS will be installed to improve staff management.

6-10

FSR on Expansion and Modernization of the MOIN Refinery Project

The unit will be equipped with a DCS to conduct central control and management for it.

DCS hardware configuration: The feasibility study will not select specific DCS, but

specifies the following requirements for configuration:

-  Operation stations: 3 sets. Each operation station shall be equipped with separate

electronic unit, display and key board.

-  Engineering stations will be used in system configuration and online system

maintenance.

-  Control stations, monitoring stations, safety barrier cabinets, and terminal cabinets

will be separately configured according to the needs of control and monitoring points.

-  Engineering stations, alarm printers and report printers will be configured according

to the needs of plant wide control system.

Separate SIS compatible with safety rating of units will be installed according to the

requirements of design specifications. System size will be determined according to actual

number of points. Safety and reliability will be the top priority of SIS, safety level of which

will meet the requirements of that of the unit. Design of SIS will incorporate system integrity,

safety, reliability, automatic and semi-automatic operation flexibility, and safety and

convenience in system maintenance to make a safe and convenient system so as to ensure safe

and long term operation of the unit.

According to the requirements of design specifications, sufficient flammable gas and

toxic gas detection sensors shall be installed according to the distribution of leakage sources

from units. Data from the sensors shall be connected with flammable gas and toxic gas

detection and alarm system (FGDS) of individual units for comprehensive monitoring on

leakage of flammable gas and toxic gas from the units in CCR.

2)

Major control loops of the unit are as following:

-  Heater control

Outlet temperature of heater radiation section constitutes cascade control with furnace

chamber temperature to control fuel gas to each section.

Flow controls will be installed on all 4 feeding streams to heater radiation section.

The heater will be equipped with zirconia oxygen analyzer to analyze and monitor

oxygen content in flue gas as well as control air flow.

-  A flow control will be installed on each steam injection for heater tubes.

Furnace chamber vacuum controls flue gas duct damper.

-  Coke tower control

Temperature control of coke tower is conducted via a specific amount of quench oil

6-11

FSR on Expansion and Modernization of the MOIN Refinery Project

injected under control to stabilize temperature and pressure in coke tower.

In order to protect radiation furnace tubes from burning out due to local superheating and

coking, surface thermocouples will be installed on tube walls to monitor tube temperature.

Armored thermocouples will be installed in the upper, middle and lower part of the coke

tower to monitors surface temperature of the tower so as to indirectly reflect level in it.

Neutron level gauges will be installed in the upper, middle and lower part of the coke

tower to measure level in it.

- Fractionator control

Fractionator top temperature constitutes cascade control with its overhead reflux flow.

Refluxes of each section will be equipped with flow and temperature controls. Each oil

collector will be equipped with a level control and double jacket level gauges.

Fractionator bottom level constitutes cascade control with inlet flow to convection

section of the heater.

Fractionator top KO drum level constitutes cascade control with gasoline outlet flow

from the unit.

3)

Major interlock protection systems of the unit are as following:

-  Upon low-low feed flow to heater and low-low pilot gas pressure, the interlock will

open heater tube for steam purging, cut off heater feed, pilot gas supply and fuel gas feed,

open heater chimney baffle, open heater bottom air duct, shut down flue gas draught fan, and

shut down air blower.

-  Upon fuel gas pressure low-low, cut fuel gas feed, open heater chimney baffle, open

heater bottom air duct, shut down flue gas draught fan, shut down air blower, and manually

switch bypass hater fuel feed.

-  Upon flue gas preheater temperature high-high, draught fan inlet flue gas temperature

high-high, draught fan inlet flue gas pressure high-high, open heater chimney baffle and shut

down flue gas draught fan.

-  Upon air blower outlet pressure low-low, open heater chimney baffle, open heater

bottom air duct, shut down flue gas draught fan, and shut down air blower.

4)

Hydraulic decoking unit will be equipped with a programmable control system as the

automatic control system for the unit.

5)

Compressor control system

6)

Size of control points in the unit

DCS detection points about 600 and control loops about 100.

6-12

FSR on Expansion and Modernization of the MOIN Refinery Project

(3)

500 KTA Continuous Catalytic Reforming Unit

1)

Description of the control system

Because the unit features in high temperature operating with hydrogen and catalyst

regeneration must be converted from a hydrogen and nitrogen environment to an oxygen

environment, the control system shall be advanced, proven and reliable. A distributed control

system (DCS) will be used in the design to conduct central monitoring, control and

management of the unit so as to ensure long term, safe production and stable operation and

achieve the objective of reduce cost and improve benefits. According to the properties of the

unit and the requirements for safe production, the following control systems will be installed:

DCS

SIS

CCS and RDAS

FGDS

AMS

Catalyst and regeneration unit will be equipped with dedicated control system provided

by reformer licensor.

A WRS will be installed to improve staff management.

The unit will be equipped with a DCS to conduct central control and management for it.

DCS hardware configuration: The feasibility study will not select specific DCS, but

specifies the following requirements for configuration:

-  Operation stations: 4 sets. Each operation station shall be equipped with separate

electronic unit, display and key board.

-  Engineering stations will be used in system configuration and online system

maintenance.

-  Control stations, monitoring stations, safety barrier cabinets, and terminal cabinets

will be separately configured according to the needs of control and monitoring points.

-  Engineering stations, alarm printers and report printers will be configured according

to the needs of plant wide control system.

Separate SIS compatible with safety rating of units will be installed according to the

requirements of design specifications. System size will be determined according to actual

number of points. Safety and reliability will be the top priority of SIS, safety level of which

will meet the requirements of that of the unit. Design of SIS will incorporate system integrity,

safety, reliability, automatic and semi-automatic operation flexibility, and safety and

convenience in system maintenance to make a safe and convenient system so as to ensure safe

6-13

FSR on Expansion and Modernization of the MOIN Refinery Project

and long term operation of the unit.

According to the requirements of design specifications, sufficient flammable gas and

toxic gas detection sensors shall be installed according to the distribution of leakage sources

from units. Data from the sensors shall be connected with flammable gas and toxic gas

detection and alarm system (FGDS) of individual units for comprehensive monitoring on

leakage of flammable gas and toxic gas from the units in CCR.

2)

Major control loops of the unit are as following:

-  Pressure control of reaction system

Pressure of the reaction system is a critical parameter in connection with stable unit

operation, reaction performance and safety of people and equipment. Reaction system

pressure (i.e., pressure in reforming product separation drum) will be set as a criterion of

control, which will be combined with compressor anti-surge control system and venting

control system into an advanced control system.

- Heater control

The heater will be equipped with oxygen analyzers to detect oxygen content in flue gas

so as to improve heat efficiency.

The heater will be equipped with air fuel ratio control and air-fuel switch sequence logic

control during heater turn-up and turndown to ensure complete combustion to minimize air

pollution. In addition, a valve-down flameout control on fuel adjustment will be configured.

3)

Major interlock protection systems of the unit are as following:

-  Upon circulation hydrogen flow low-low, shut down all reforming reaction heaters

and cut off reforming feed.

-  Upon depentanizer reboiler feed flow low-low, shut down reboiler.

-  Upon heater pilot fuel gas pressure low-low, shut down heater.

4)

Control system for catalyst and regeneration unit

Catalyst and regeneration process is critical to the operation of high vacuum and high

severity continuous catalytic reforming process. It applies a catalyst regeneration control

system. Its control and interlock protection belongs to patent technology of licensor, which

will be strictly followed during implementation.

5)

Size of control points in the unit

DCS detection points about 650 and control loops about 80.

SIS detection points about 85 and control loops about 24.

FGDS detection points about 120.

6-14

FSR on Expansion and Modernization of the MOIN Refinery Project

CCS detection points about 330 and control loops about 10.

(4)

1,300 KTPA Diesel Hydrofining Unit

1)

Description of the control system

Besides continuous operation and flammable, explosive, corrosive and hazard fluids

common in petrochemical units, reaction section of the unit also features in high temperature,

medium pressure and hydrogen presence. Selection and installation of instruments and

electrical shall be in line with the process properties of the unit to ensure uninterruptable, safe

and reliable operation so as to achieve safe production, promote operation management and

better improve unit operation benefits. According to the properties of the unit and the

requirements for safe production, the following control systems will be installed:

DCS

SIS

CCS and RDAS

FGDS

AMS

A WRS will be installed to improve staff management.

a)

The unit will be equipped with a DCS to conduct central control and management for

it.

DCS hardware configuration: The feasibility study will not select specific DCS, but

specifies the following requirements for configuration:

-  Operation stations: 3 sets. Each operation station shall be equipped with separate

electronic unit, display and key board.

-  Engineering stations will be used in system configuration and online system

maintenance.

-  Control stations, monitoring stations, safety barrier cabinets, and terminal cabinets

will be separately configured according to the needs of control and monitoring points.

-  Engineering stations, alarm printers and report printers will be configured according

to the needs of plant wide control system.

b)

Separate SIS compatible with safety rating of units will be installed according to the

requirements of design specifications. System size will be determined according to

actual number of points. Safety and reliability will be the top priority of SIS, safety

level of which will meet the requirements of that of the unit. Design of SIS will

incorporate system integrity, safety, reliability, automatic and semi-automatic

6-15

FSR on Expansion and Modernization of the MOIN Refinery Project

operation flexibility, and safety and convenience in system maintenance to make a safe

and convenient system so as to ensure safe and long term operation of the unit.

c)

According to the requirements of design specifications, sufficient flammable gas and

toxic gas detection sensors shall be installed according to the distribution of leakage

sources from units. Data from the sensors shall be connected with flammable gas and

toxic gas detection and alarm system (FGDS) of individual units for comprehensive

monitoring on leakage of flammable gas and toxic gas from the units in CCR.

d)

CCS

According to the practical needs of diesel section of the unit, circulation hydrogen

compressor package will be equipped with a special compressor control system (CCS) to

execute load control, process control and interlock protection functions. The system is capable

of communication with DCS. CCS will apply TMR or DMR redundant and fault tolerant

system and use special application software with event sequence recording function. CCS will

be supplied by compressor package supplier.

CCS shall communicate with DCS. CCS operation shall be monitored on DCS displays.

Signal transmission between CCS and DCS will use RS485, Modbus RTU communication

protocol.

2)

Major control loops of the unit are as following:

-  Feed stock buffer drum will be equipped with level – flow rate cascade control.

Nitrogen purging system will use pressure split range control.

-  Hydrogenation feed heater outlet temperature cascades with fuel gas pressure.

-  Hydrogenator will be equipped with multiple thermocouples to detect reactor bed

temperature. Hydrogenation feed heater will be equipped with furnace tube surface

temperature detection thermocouples.

-  Heater will be equipped with chamber vacuum control and zircornia oxygen analyzer

for flue gas to control heater combustion efficiency.

-  Fractionator will be equipped with pressure control, overhead temperature cascading

with reflux flow and bottom level cascading with product flow at the outlet of the unit to

ensure product quality and stable fractionators operation.

-  Pressure control of hydrogenation system will use low value selection through the

adjustment of reflux to fresh hydrogen compressor.

-  Where flammable gas and H2S leakage or accumulation is possible, flammable gas

and H2S content detection transmitters shall be installed with central display and alarm in

CCR.

6-16

FSR on Expansion and Modernization of the MOIN Refinery Project

3)

Major interlock protection systems of the unit are as following:

-  Heater fuel gas pressure low-low and heater chamber pressure extra high interlocks.

-  Circulation hydrogen compressor inlet KO drum high-high interlock.

-  Compressor package safety interlock protection system.

4)

Size of control points in the unit

DCS detection points about 500 and control loops about 60.

SIS detection points about 200.

FGDS detection points about 50.

(5)

550 KTA Naphtha Hydrotreating Unit

1)

Description of the control system

Besides continuous operation and flammable, explosive, corrosive and hazard fluids

common in petrochemical units, reaction section of the unit also features in high temperature,

medium pressure and hydrogen presence. Selection and installation of instruments and

electrical shall take this into consideration to ensure long term and safe operation, minimize

process operators and instrument maintenance staff so as to improve system reliability,

achieve safe production, promote operation management and better improve unit operation

benefits. According to the properties of the unit and the requirements for safe production, the

following control systems will be installed:

DCS

SIS

CCS

FGDS

AMS

WRS

a)

The unit will be equipped with a DCS to conduct central control and management for

it.

DCS hardware configuration: The feasibility study will not select specific DCS, but

specifies the following requirements for configuration:

-  Operation stations: 2 sets. Each operation station shall be equipped with separate

electronic unit, display and key board.

-  Engineering stations will be used in system configuration and online system

maintenance.

6-17

FSR on Expansion and Modernization of the MOIN Refinery Project

-  Control stations, monitoring stations, safety barrier cabinets, and terminal cabinets

will be separately configured according to the needs of control and monitoring points.

-  Engineering stations, alarm printers and report printers will be configured according

to the needs of plant wide control system.

b)

Separate SIS compatible with safety rating of units will be installed according to the

requirements of design specifications. System size will be determined according to

actual number of points. Safety and reliability will be the top priority of SIS, safety

level of which will meet the requirements of that of the unit. Design of SIS will

incorporate system integrity, safety, reliability, automatic and semi-automatic

operation flexibility, and safety and convenience in system maintenance to make a safe

and convenient system so as to ensure safe and long term operation of the unit.

c)

According to the requirements of design specifications, sufficient flammable gas and

toxic gas detection sensors shall be installed according to the distribution of leakage

sources from units. Data from the sensors shall be connected with flammable gas and

toxic gas detection and alarm system (FGDS) of individual units for comprehensive

monitoring on leakage of flammable gas and toxic gas from the units in CCR.

2)

Major control loops of the unit are as following:

-  Feed stock buffer tank fuel sealing system uses pressure split range control.

-  Hydrogenation feed heater outlet temperature cascades with fuel gas pressure.

-  Hydrogenator will be equipped with multiple thermometers to detect reactor bed

temperature. Hydrogenation feed heater will be equipped with furnace tube surface

temperature detection thermocouples.

-  Heater will be equipped with chamber vacuum control and zircornia oxygen analyzer

for flue gas to improve heater combustion efficiency.

-  Fractionator will be equipped with pressure control, overhead temperature cascading

with reflux flow and bottom level cascading with partial naphtha product flow at the outlet of

the unit to ensure product quality and stable fractionators operation.

-  Where flammable gas and H2S leakage or accumulation is possible, flammable gas

and H2S content detection transmitters shall be installed with central display and alarm in

CCR.

3)

Major interlock protection systems of the unit are as following:

-  Heater fuel gas pressure low-low and heater chamber pressure extra high interlocks.

-  Circulation hydrogen compressor inlet KO drum high-high interlock.

6-18

FSR on Expansion and Modernization of the MOIN Refinery Project

-  Circulation hydrogen compressor safety interlock protection system.

4)

Scope of supply for instruments and control systems supplied with equipment

packages

Instruments for compressor package will be supplied with the equipment.

5)

Size of control points in the unit

DCS detection points about 580 and control loops about 50.

SIS detection points about 200 and control loops about 60.

FGDS detection points about 30.

(6)

900 KTA hydrocracking unit

1)

Description of the control system

The unit features in complex process technology with flammable and explosive fluids

requiring rigorous operation safety. Therefore, automatic control system shall not only have

perfect control capabilities but also possess high reliability and high safety for safe, reliable

and long term operation of the units so as to improve reliability of the automatic control

system, ensure safe production, promote operation management level and yield better

economic returns from unit operation. According to the properties of the unit and the

requirements for safe production, the following control systems will be installed:

DCS

SIS

CCS

FGDS

AMS

A WRS will be installed to improve staff management.

a)

The unit will be equipped with a DCS to conduct central control and management for

it.

DCS hardware configuration: The feasibility study will not select specific DCS, but

specifies the following requirements for configuration:

-  Operation stations: 4 sets. Each operation station shall be equipped with separate

electronic unit, display and key board.

-  Engineering stations will be used in system configuration and online system

maintenance.

-  Control stations, monitoring stations, safety barrier cabinets, and terminal cabinets

6-19

FSR on Expansion and Modernization of the MOIN Refinery Project

will be separately configured according to the needs of control and monitoring points.

-  Engineering stations, alarm printers and report printers will be configured according

to the needs of plant wide control system.

b)

Separate SIS compatible with safety rating of units will be installed according to the

requirements of design specifications. System size will be determined according to

actual number of points. Safety and reliability will be the top priority of SIS, safety

level of which will meet the requirements of that of the unit. Design of SIS will

incorporate system integrity, safety, reliability, automatic and semi-automatic

operation flexibility, and safety and convenience in system maintenance to make a safe

and convenient system so as to ensure safe and long term operation of the unit.

c)

According to the requirements of design specifications, sufficient flammable gas and

toxic gas detection sensors shall be installed according to the distribution of leakage

sources from units. Data from the sensors shall be connected with flammable gas and

toxic gas detection and alarm system (FGDS) of individual units for comprehensive

monitoring on leakage of flammable gas and toxic gas from the units in CCR.

d)

CCS

Circulating hydrogen compressor package will be equipped with a special compressor

control system (CCS) to execute governing, anti-surge control, load control, process control,

and interlock protection functions. The system is capable of communication with DCS. CCS

will apply TMR or DMR redundant and fault tolerant system and use special application

software, e.g., RPM control and anti-surge control with event sequence recording function.

CCS will be supplied by compressor package supplier.

CCS shall communicate with DCS. CCS operation shall be monitored on DCS displays.

Signal transmission between CCS and DCS will use RS485, Modbus RTU communication

protocol.

e)

RDAS

RDAS will be used in online monitoring of rotary equipment, e.g., circulating hydrogen

compressor and will conduct analysis and diagnostic on equipment performance.

Major parameters to be monitored for rotary equipment include shaft vibration, shaft

displacement, phase, and rotational speed. Operators may directly read rotary equipment data

from the online monitoring equipment.

Signal input and data processors for equipment analysis and diagnostic will be installed

in CCR. Equipment operation engineer may conduct online diagnostics and analysis on

equipment operation performance.

6-20

FSR on Expansion and Modernization of the MOIN Refinery Project

RDAS will hardwire any data participating interlock protection to CCS. Other

parameters will be communicated to CCS.

f)

Equipment package control system (PLC)

PLC system for small but independent equipment, e.g., feed oil filter and circulating

hydrogen compressor inlet coalescer will usually be supplied with equipment packages. Such

system will be usually installed in local explosion proof and weather proof control panels

(cabinets) and communicate with DCS via redundant serial communication interface with

MODBUS protocol.

2)

Major control loops of the unit are as following:

-  Feed rate control

A level-flow rate cascade ratio control plan will be configured according to feeding

property of the unit.

-  Pressure control for reaction system

Benchmark pressure control point of reaction system is configured on circulating

hydrogen compressor inlet KO drum to control reaction system pressure through control of

fresh hydrogen makeup rate.

- Reactor temperature control

Reactor inlet temperature is controlled through the control of outlet temperature of

reactor feed heater, while reactor bed temperature will be controlled by the flow rate of

hydrogen injected via cold hydrogen injection point of the reactor.

-  Level monitoring and control of thermal high pressure separator

Based on the rigorous conditions of high temperature and high pressure in the thermal

high pressure separator:

Multiple level detection and protection (differential pressure and high pressure magnetic

float level field observation) measures will be configured to ensure highly reliable and stable

level control for the thermal high pressure separator.

-  Level and interface monitoring and control of cold high pressure separator

Its level and interface will be controlled by the openness of the high pressure/high

pressure drop regulating valve. Double level control valves will be configured.

Based on the operation conditions of cold high pressure separator, multiple level

detection and protection (HP buoy level gauge control, HP level switch interlock protection

and high pressure magnetic float level field observation) measures will be configured to

ensure stable control of level and interface in the HP separator.

-  Stripper bottom level control

6-21

FSR on Expansion and Modernization of the MOIN Refinery Project

Stripper bottom level cascades with fractionators feed flow rate. Advantages of the plan

is when stripper bottom level fluctuates within permissible range, fractionators feed flow rate

will be controlled according to fixed rate so as to ensure stable operation of upstream and

downstream processes.

3)

Major interlock protection systems of the unit are as following:

-  Emergency relieving safety interlock system.

-  Reaction feed heater safety interlock system.

-  Fractionation feed heater safety interlock system

-  Hydrogenation feed pump safety interlock system.

-  Lean solvent pump safety interlock system.

-  Fresh hydrogen compressor safety interlock system.

4)

Size of control points in the unit

DCS detection points about 900 and control loops about 150.

SIS detection points about 260 and control loops about 50.

FGDS detection points about 50.

(7)

150 KTA Isomerization Unit

1)

Description of the control system

The unit features in complex process technology with high product quality requirements.

In order to ensure safe, stable, long term, full load, and high quality operation of the unit, it is

required to use new generation distributed control system (DCS) to control, monitor, record,

and alarm the whole unit.  Operation status of major compressors and pumps will be

displayed via DCS. In order to ensure unit and operator safety and safe operation, the

following control systems will be installed according to the properties of the unit and the

requirements for safe production:

DCS

SIS

CCS

FGDS

AMS

A WRS will be installed to improve staff management.

a)

The unit will be equipped with a DCS to conduct central control and management for

it.

6-22

FSR on Expansion and Modernization of the MOIN Refinery Project

DCS hardware configuration: The feasibility study will not select specific DCS, but

specifies the following requirements for configuration:

-  Operation stations: 2 sets. Each operation station shall be equipped with separate

electronic unit, display and key board.

-  Engineering stations will be used in system configuration and online system

maintenance.

-  Control stations, monitoring stations, safety barrier cabinets, and terminal cabinets

will be separately configured according to the needs of control and monitoring points.

-  Engineering stations, alarm printers and report printers will be configured according

to the needs of plant wide control system.

b)

Separate SIS compatible with safety rating of units will be installed according to the

requirements of design specifications. System size will be determined according to

actual number of points. Safety and reliability will be the top priority of SIS, safety

level of which will meet the requirements of that of the unit. Design of SIS will

incorporate system integrity, safety, reliability, automatic and semi-automatic

operation flexibility, and safety and convenience in system maintenance to make a safe

and convenient system so as to ensure safe and long term operation of the unit.

c)

According to the requirements of design specifications, sufficient flammable gas and

toxic gas detection sensors shall be installed according to the distribution of leakage

sources from units. Data from the sensors shall be connected with flammable gas and

toxic gas detection and alarm system (FGDS) of individual units for comprehensive

monitoring on leakage of flammable gas and toxic gas from the units in CCR.

2)

Major control loops of the unit are as following:

Most control loops in the unit will use proven single loop fixed set point control with

special controls as following:

-  Reaction feed heater outlet temperature cascades with fuel gas pressure.

-  Isomerization reactor will be equipped with multiple thermometers to detect bed

temperature. Feed heater will be equipped with furnace tube surface temperature detection

thermocouples.

-  Heater will be equipped with chamber vacuum control and zircornia oxygen analyzer

for flue gas to control heater combustion efficiency.

-  Stabilizer will be equipped with overhead pressure control and bottom level control.

Stabilizer reflux drum level cascades with reflux flow to ensure stable operation of the tower.

-  Where flammable gas and H2S leakage or accumulation is possible, flammable gas

6-23

FSR on Expansion and Modernization of the MOIN Refinery Project

and H2S content detection transmitters shall be installed with central display and alarm in

CCR.

3)

Major interlock protection systems of the unit are as following:

-  Upon upsetting in reaction section, emergency venting and relieving interlock system

will be initiated.

-  Heater fuel gas pressure low-low and heater chamber pressure extra high interlocks.

-  Circulation hydrogen compressor inlet KO drum high-high interlock.

-  Circulating hydrogen compressor safety interlock protection system.

4)

Size of control points in the unit

DCS detection points about 150 and control loops about 30.

SIS detection points about 80 and control loops about 20.

FGDS detection points about 30.

(8)

25 KTA H

Production unit

2

1)

Description of the control system

Fluids in the unit feature in flammable and explosive requiring advanced, proven and

reliable control system. Therefore, PC based DCS will be used to conduct central

management and distributed control of the whole unit so as to improve system reliability and

to facilitate operation optimization during normal production as well as long term, safe and

stable operation. According to the properties of the unit and the requirements for safe

production, the following control systems will be installed:

DCS

SIS

CCS

FGDS

AMS

A WRS will be installed to improve staff management.

a)

The unit will be equipped with a DCS to conduct central control and management for

it.

DCS hardware configuration: The feasibility study will not select specific DCS, but

specifies the following requirements for configuration:

-  Operation stations: 3 sets (for H2 Production and PSA). Each operation station shall

6-24

FSR on Expansion and Modernization of the MOIN Refinery Project

be equipped with separate electronic unit, display and key board.

-  Engineering stations will be used in system configuration and online system

maintenance.

-  Control stations, monitoring stations, safety barrier cabinets, and terminal cabinets

will be separately configured according to the needs of control and monitoring points.

-  Engineering stations, alarm printers and report printers will be configured according

to the needs of plant wide control system.

b)

Separate SIS compatible with safety rating of units will be installed according to the

requirements of design specifications. System size will be determined according to

actual number of points. Safety and reliability will be the top priority of SIS, safety

level of which will meet the requirements of that of the unit. Design of SIS will

incorporate system integrity, safety, reliability, automatic and semi-automatic

operation flexibility, and safety and convenience in system maintenance to make a safe

and convenient system so as to ensure safe and long term operation of the unit.

c)

According to the requirements of design specifications, sufficient flammable gas and

toxic gas detection sensors shall be installed according to the distribution of leakage

sources from units. Data from the sensors shall be connected with flammable gas and

toxic gas detection and alarm system (FGDS) of individual units for comprehensive

monitoring on leakage of flammable gas and toxic gas from the units in CCR.

d)

CCS is responsible for interlock protection of the package and communication with

DCS. It shall be supplied by the compressor supplier with the package.

2)

Major control loops of the unit are as following:

-  Reformer water/carbon ratio control: A water/carbon ratio control will be configured

for steam flow rate and feed gas flow rate into the reformer. Total carbon value of the feed gas

will be analyzed on real time by an online analyzer and be determined against feed gas flow

rate in DCS.

-  Reformer outlet temperature control: Reformer outlet temperature adjustment will be

done by a cascade control between reformer outlet reforming gas temperature and fuel gas

(primary stream and secondary stream) flow rate. During H2 Production unit startup,

temperature of reforming gas leaving the reformer cascades with system secondary fuel gas.

When PSA gas is switched in, temperature of reforming gas leaving the refor mer will cascade

with the primary fuel gas stream. Switching of both conditions above will be executed by

switches.

-  Steam system control: Waste heat boiler in the steam system will be controlled by

6-25

FSR on Expansion and Modernization of the MOIN Refinery Project

boiler level, boiler feed water flow rate and boiler steam flow rate.

-  Load and temperature management system: H2 Production capacity will be managed

via feed gas flow rate, steam flow rate, reformer air and fuel supply adjustment, maintaining

stable reformer water/carbon ratio, and reforming gas temperature adjustment.

-  PSA outlet will be equipped with an online hydrogen content analyzer.

-  Where flammable (toxic) gas leakage is possible, e.g., blow down points and pump

station, flammable (toxic) gas detectors with display and alarm in CCR will be installed.

3)

Major interlock protection systems of the unit are as following:

-  Compressor shaft temperature high-high, lub oil pressure low-low and machinery

vibration interlock protection will initiate SIS to trigger a compressor shutdown.

4)

Size of control points in the unit

DCS detection points about 400 and control loops about 65.

SIS detection points about 200 and control loops about 100.

FGDS detection points about 50.

(9)

Sulfur Recovery Unit

1)

Description of the control system

The unit consists of acid water stripping, solvent regeneration and sulfur recovery

sections. It is an environmental protection unit with its social benefits far bigger than its

economic benefits. Only its safe, stable and long term operation will ensure emission method

and concentration of major pollutants, especially sulfur, SO2 and other sulfur compounds

from the refinery meet national air pollutants emission environmental protection standard.

The unit features in advanced and complex process with toxic, flammable and explosive

process fluids. Any accidents during operation would result in injuries. Therefore, there are

strict requirements for the reliability and automatic level of field instruments and control

system. Automatic instruments selected shall be reliable in quality, advanced in technology,

reasonable in economy and stable in performance with proven application experience and

technical support to meet the requirements of the unit for automatic instruments. According to

the properties of the unit and the requirements for safe production, the following control

systems will be installed:

DCS

SIS

CCS and RDAS

FGDS

6-26

FSR on Expansion and Modernization of the MOIN Refinery Project

AMS

A WRS will be installed to improve staff management.

a)

The unit will be equipped with a DCS to conduct central control and management for

it.

DCS hardware configuration: The feasibility study will not select specific DCS, but

specifies the following requirements for configuration:

-  Operation stations: 4 sets. Each operation station shall be equipped with separate

electronic unit, display and key board.

-  Engineering stations will be used in system configuration and online system

maintenance.

-  Control stations, monitoring stations, safety barrier cabinets, and terminal cabinets

will be separately configured according to the needs of control and monitoring points.

-  Engineering stations, alarm printers and report printers will be configured according

to the needs of plant wide control system.

b)

Separate SIS compatible with safety rating of units will be installed according to the

requirements of design specifications. System size will be determined according to

actual number of points. Safety and reliability will be the top priority of SIS, safety

level of which will meet the requirements of that of the unit. Design of SIS will

incorporate system integrity, safety, reliability, automatic and semi-automatic

operation flexibility, and safety and convenience in system maintenance to make a safe

and convenient system so as to ensure safe and long term operation of the unit.

c)

According to the requirements of design specifications, sufficient flammable gas and

toxic gas detection sensors shall be installed according to the distribution of leakage

sources from units. Data from the sensors shall be connected with flammable gas and

toxic gas detection and alarm system (FGDS) of individual units for comprehensive

monitoring on leakage of flammable gas and toxic gas from the units in CCR.

2)

Major control loops of the unit are as following:

-  Ratio control system

According to sulfur conversion principle, when the ratio of H2S and SO

in process gas

2

from the combustion furnace is controlled at 2:1 under proper air supply, element sulfur yield

in the converter will be the highest. The ratio control system allocates air supply according to

the chemical equivalent of feed acid gas volume, i.e., conducts acid gas and air ratio control.

Because H

S in acid gas varies during operation, error of ratio control system is inevitable, a

2

6-27

FSR on Expansion and Modernization of the MOIN Refinery Project

quality control system is configured besides the ratio control system to maintain H

S/ SO

2

2

ratio.

Air volume adjustment in the program is divided into two parts: The first is the ratio

control system to adjust air volume according to acid gas volume to regulate acid gas/air ratio.

The second is the cascade adjustment system between H

S/SO

online ratio analyzer and air

2

2

volume for the correction of air and acid gas proportion to ensure close H

S/SO

ratio during

2

2

operation.

-  Combustion furnace blower applies typical anti-surge control.

-  Primary condensing cooler applies double impulse control, i.e., steam flow rate and

level to control water supply valve.

-  MP steam drum of waste heat boiler for acid gas combustion furnace applies triple

impulse control.

-  Tail gas incinerator chamber temperature cascades with fuel gas pressure.

-  Hydrogenation type acid water stripping feed water pump outlet flow constitutes

ratio control with primary stripper side line total purification water flow and primary stripper

stripping steam flow.

-  Hydrogenation type primary stripper overhead pressure cascades with side line acid

water flow.

-  Hydrogenation type primary stripper overhead temperature difference cascades with

acid gas pressure.

-  Non hydrogenation type primary stripper overhead hot feed constitutes ratio control

with primary stripper steam flow.

-  Solvent regenerator rich solution flow constitutes ratio control with regenerator

bottom heating steam flow.

-  Solvent regenerator overhead reflux drum level cascades with overhead reflux flow.

3)

Major interlock protection systems of the unit are as following:

- SRU shutdown.

- Fan shutdown.

-  Liquid sulfur deaeration shutdown.

-  Tail gas treatment shutdown.

Size of control points in the unit

DCS detection points about 500 and control loops about 120.

SIS detection points about 120 and control loops about 90.

6-28

FSR on Expansion and Modernization of the MOIN Refinery Project

FGDS detection points about 60.

(10)

Dry Gas / LPG Treatment Unit

1)

Description of the control system

The unit consists of dry gas scrubbing and LPG Treatment sections according to process

with flammable, explosive, toxic and corrosive process fluids. Only stable and long term

operation of the unit would ensure on-spec emission methods and concentration of major

pollutants from refineries. Therefore, control systems and filed instruments designed shall be

advanced in technology, proven and reliable to meet the requirements for continuous

operation. According to the properties of the unit and the requirements for safe production,

the following control systems will be installed:

DCS

FGDS

AMS

A WRS will be installed to improve staff management.

a)

The unit will be equipped with a DCS to conduct central control and management for

it.

DCS hardware configuration: The feasibility study will not select specific DCS, but

specifies the following requirements for configuration:

-  Operation stations: 2 sets. Each operation station shall be equipped with separate

electronic unit, display and key board.

-  Engineering stations will be used in system configuration and online system

maintenance.

-  Control stations, monitoring stations, safety barrier cabinets, and terminal cabinets

will be separately configured according to the needs of control and monitoring points.

-  Engineering stations, alarm printers and report printers will be configured according

to the needs of plant wide control system.

b)

Separate SIS compatible with safety rating of units will be installed according to the

requirements of design specifications. System size will be determined according to

actual number of points. Safety and reliability will be the top priority of SIS, safety

level of which will meet the requirements of that of the unit. Design of SIS will

incorporate system integrity, safety, reliability, automatic and semi-automatic

operation flexibility, and safety and convenience in system maintenance to make a safe

and convenient system so as to ensure safe and long term operation of the unit.

6-29

FSR on Expansion and Modernization of the MOIN Refinery Project

c)

According to the requirements of design specifications, sufficient flammable gas and

toxic gas detection sensors shall be installed according to the distribution of leakage

sources from units. Data from the sensors shall be connected with flammable gas and

toxic gas detection and alarm system (FGDS) of individual units for comprehensive

monitoring on leakage of flammable gas and toxic gas from the units in CCR.

2)

Major control loops of the unit are as following:

-  Product outlet pressure control.

-  LPG scrubbing tower interface control and caustic solution circulation flow rate

control.

-  Water scrubbing circulation flow rate control.

-  Where flammable gas and H

S leakage or accumulation is possible, flammable gas

2

and H2S content detection transmitters shall be installed with central display and alarm in

CCR.

3)

Size of control points in the unit

DCS detection points about 300 and control loops about 40.

FGDS detection points about 25.

6.4.3

Instrument selection and scope of package supply

Describe scope of detection and control instruments for the unit and specify instrument

types. Specify technical requirements and scope of manufacturer supply of instruments and

control systems for package process equipment.

Select proper instruments of reliable performance, advanced technology, reasonable

price, and satisfactory after-sale service and technical support from famous global

manufacturers.

Smart field instruments using 4

~

20mA DC standard signals and compatible with HART

protocol are preferred.

Intrinsic safe instruments with explosion proof rating not lower than iaIICT4 are

preferred for hazardous areas. When intrinsic safe instruments are not available, explosion

proof models with explosion proof rating not lower than dIICT4 may be used. ON/OFF

instruments will be of explosion proof types.

Control system will use new generation DCS of current configuration.

SIS comprising redundant/fault tolerant PLCs shall be of accident safe type and

independent from DCS.

Based on the principle of fewer but better and not choosing at random, configuration of

6-30

FSR on Expansion and Modernization of the MOIN Refinery Project

online analyzers shall be in line with process requirements of each unit and the requirements

of the customer.

Surge protector shall use imported products.

Safety barriers shall be of isolation types.

6.4.3.1

2,000KTPA ADU and 1,500 KTPA VDU

Most field instruments in the unit will be of intrinsic safe models and some will be of

explosion proof types.

All temperature, pressure and differential pressure transmitters will be of smart types.

Differential pressure type flow meters are preferred in flow measurement. Mass flow

meters are preferred for the measurement of major materials at unit BL/plant boundary. Flow

rate measurement for high temperature and viscous fluid (temperature =200

) will use

wedge type flow meters. Flow rate measurement for medium and low temperature viscous

fluid (temperature < 200

) will use target flow transmitter. Flow rate measurement of steam

and fuel gas at the inlet of the unit and blower will use averaging pitot tube flow meter.

Level gauges will normally use differential pressure or flange type differential pressure

transmitters. For small range levels, electric external buoy or pneumatic external buoy level

gauges will be used.

Normally regulating valves to be used include cage type regulating valves, pneumatic

piston cutoff valve, pneumatic long travel actuator, and self powered regulating valve.

Regulating valves for high flow viscous oil fluid usually use eccentric rotary valves.

Thermocouples in heater tube wall will be of double edge models.

Online analyzers: Naphtha dry point analyzers, online pH meters and zirconia analyzers

for heater flue gas will be installed according to process requirements.

Safety detection instruments: Where flammable gas leakage is possible, e.g., blow down

points, compressor room and pump station, flammable gas detectors will be installed with

signals transmitted to CCR for display and alarm in FGDS.

Input safety barriers for temperature adjustment loops will use isolation types with

temperature transmitting functions.

In order to meet the high requirements of process for automatic control systems, world

advanced, proven and reliable DCS will be used in the unit.

SIS shall be product certified by corresponding international safety qualification

organizations. Safety rating of the systems selected shall not be lower than that of process

unit.

6.4.3.2

700 KTPA Delayed Coking Unit

6-31

FSR on Expansion and Modernization of the MOIN Refinery Project

Most field instruments in the unit will be of intrinsic safe models and some will be of

explosion proof types.

Temperature measurement instruments: Double metal thermometers will be used for

field temperature measurement. Special enclosed thermometer protection thermowells shall

be used for field temperature measurement at HP locations.

Remote temperature signals will be equipped with thermocouples. Temperature

measurement of compressors will usually use RTD. Heater tube surface temperature

measurement will use knife type armored thermocouples. Column wall surface temperature

will be measured by armored surface thermocouples, thermowell material of which will be

determined according to temperature to be measured.

Pressure gauges: Normally, bourdon tube pressure gauges will be used. Stainless steel

safe pressure gauges will be used at HP points. Diaphragm type micro pressure gauges will be

used in furnace chamber pressure detection. Remote pressure signals will be transmitted by

pressure transmitters or DP transmitters. Diaphragm type pr oducts shall be used for viscous,

corrosive and crystalline fluids. Outlet of power equipment or other locations with vibration

shall use vibration proof pressure gauges.

Flow meters: Normally, throttling devices with DP transmitters will be used.

Measurement of critical flow rate for materials entering/leaving unit will be done by

volumetric or mass flow meters. Large size water flow measurement entering unit will use

electromagnetic flow meters. Small pipes or clean fluids will be measured by metal tube float

flow meter. Flow rate of viscous fluids will be measured by wedge type flow meters or target

flow meters.

Level (interface) gauges: Local measurement will use quartz tube level gauges. Wide

range measurement will use magnetic float level (interface) gauges. Wide range remote level

measurement will use double flange DP transmitters. Elevated water tanks will be equipped

with radar level gauges. Critical or interlocked level measurements will use float ball level

switches.

Selection of actuators

-  Pneumatic diaphragm regulating valves are normally used. Regulating valves for HP

and high differential pressure locations shall use imported products. Regulating valves for

high differential pressure locations shall use high pressure drop resistant, vacuum proof and

low noise regulating angle valve. Eccentric rotary valves, angle valves or T regulating valves

shall be selected according to fluids or process requirements.

-  Cutoff valves for interlocks shall use tight closure single cylinder ON/OFF ball

valves equipped with single electric solenoid valves and valve position transponders.

Temperature, pressure and DP transmitters: Use smart transmitters.

6-32

FSR on Expansion and Modernization of the MOIN Refinery Project

Online analyzers: Use imported zirconia oxygen analyzer to measure oxygen content of

flue gas in furnace chamber.

Safety barriers: Use isolating type safety barriers.

Safety instruments: Flammable gas detectors and toxic gas transmitter sensors shall be

installed in unit area with signals sent to CCR.

In order to meet the high requirements of process for automatic control systems, world

advanced, proven and reliable DCS will be used in the unit.

SIS shall be product certified by corresponding international safety qualification

organizations. Safety rating of the systems selected shall not be lower than that of process

unit.

Supporting instruments and control system for packaged process equipment:

-  Design of control systems for compressors, HP water pumps and hydraulic decoking

will be provided by supplier.

6.4.3.3

500 KTA Continuous Catalytic Reforming Unit

Advanced, reliable and easy to install and operate instruments will be selected for the

unit according to process conditions and requirements. Electric instruments will be of intrinsic

safe or explosion proof models in line with explosion proof rating of process atmosphere.

Measurement elements exposed to corrosive fluids will use corrosion resistant materials.

Metering gauges of different accuracies meeting industrial standards will be selected

according to different effluent requirements.

Local temperature indication will use directional double metal thermometers. Remote

temperature indication or control will use E or K type thermocouples according to IEC

standard.

Temperature measurement usually uses retractable armored thermocouples. Temperature

measurement for regenerator will use flexible thermocouples. Surface temperature

measurement for equipment or pipelines will use surface thermocouples. Armored

thermocouples will be used in reactor.

For temperature measurement points in heater and regenerator, multiplex field collectors

with communication bus connections with DCS will be used for temperature indication.

Thermocouples in heater tube wall will be of double edge models.

Local pressure indication will use pressure gauges. Vacuum indication will use capsule

pressure gauges. Remote pressure indication and control will use pressure transmitters.

Interlock and alarm will use pressure switches.

Flow rates are usually measured by flanged standard throttling elements with DP

transmitters. Mass flow meters are preferred for the measurement of major materials at unit

6-33

FSR on Expansion and Modernization of the MOIN Refinery Project

BL. Flow rate measurement for high temperature and viscous fluid (temperature = 200 ) will

use wedge type flow meters. Flow rate measurement for medium and low temperature viscous

fluid (temperature < 200 ) will use target flow transmitter. Flow rate measurement of steam

and fuel gas at the inlet of the unit and blower will use averaging pitot tube flow meter. Flow

rate indication for nitrogen back purge to instrument measurement pulse line will use local

glass rotameter. Metal rotameters will be used for locations only requiring field indication and

CCR alarm.

Local level indication will use double color level glass. Remote measurement will use

double flange DP transmitters and buoy level/interface transmitters. Interlock and alarm will

use level switches. Level measurement for catalyst in regenerator will use radioactive level

gauge, radioactive level switch and capacitor level gauge.

In order to reduce energy consumption, improve heater heat efficiency, zirconia oxygen

analyzers will be used in heater chamber and flue gas duct.

Where necessary, hydrogen, oxygen and water analyzers will be installed.

Flammable gas alarms will be installed at location where flammable gas leakage is

possible.

Pneumatic and cylinder type actuators will be used. Single or double seat regulating

valve, angle valve, butterfly valve, eccentric rotary valve, and ball valves shall be selected

according to requirements of different process parameters. Special ball valves and V-notched

ball valves or special rotary valves will be used in catalyst pipelines. Large size gas control

will use butterfly valve. Large flow and viscous oil fluids will use eccentric rotary regulating

valve.

Input safety barriers for temperature adjustment loops will use isolation types with

temperature transmitting functions.

In order to meet the high requirements of process for automatic control systems, world

advanced, proven and reliable DCS will be used in the unit.

SIS shall be product certified by corresponding international safety qualification

organizations. Safety rating of the systems selected shall not be lower than that of process

unit.

Supporting instruments and control system for packaged process equipment:

-  Interlock hopper control system (patent control equipment).

-  Catalyst regeneration control and interlock protection system (patent control

equipment).

6.4.3.4

1,4 000KTPA kerosene and diesel hydrofining unit

Most field instruments in the unit will be of intrinsic safe models and some will be of

6-34

FSR on Expansion and Modernization of the MOIN Refinery Project

explosion proof types.

All temperature, pressure and differential pressure transmitters will be of smart types.

Armored RTDs/thermocouples are preferred in remote temperature measurement.

Flexible thermocouples will be used in reactor bed temperature measurement. Surface

thermocouples will be used in equipment and pipeline surface temperature measurement.

DP flow meters are preferred in flow measurement. Vortex flow meters, electromagnetic

flow meters, mass flow meters, averaging pitot tube flow meters, and ultrasonic flow meters

may also be selected according to requirements. Mass flow meters shall be used for major

process materials at unit BL and flow requiring accurate measurements.

Level measurement with range less than 1500 mm will usually use external buoy type

level transmitters. Buoy type level transmitters, magnetic float level gauges and level glasses

usually use domestic products. Level gauges with proper certified safety ratings will be used

at critical, HP or interlocked high/low level detection and control points. Level measurement

for wide range HP vessels will use HP double flange level transmitters and narrow range HP

vessels will use HP buoy level transmitters.

Circulating hydrogen compressor inlet pipeline will be equipped with online hydrogen

analyzer.

Regulating valves use pneumatic diaphragm actuators normally with straight run valve

bodies. Angle regulating valves are used at HP and high pressure drop applications.

Regulating valves are usually equipped with smart electric/pneumatic valve positioners.

Input safety barriers for temperature adjustment loops will use isolation types with

temperature transmitting functions.

In order to meet the high requirements of process for automatic control systems, world

advanced, proven and reliable DCS will be used in the unit.

SIS shall be product certified by corresponding international safety qualification

organizations. Safety rating of the systems selected shall not be lower than that of process

unit.

Design principle for F & G system: Separate from DCS and SIS and capable of

communication with DCS.

Safety barriers: Use isolation type safety barriers.

Scope of instruments and control system to be supplied with equipment packages.

Instruments for compressor package will be supplied with the equipment package.

6.4.3.5

550 KTA Naphtha Hydrotreating Unit

Most field instruments in the unit will be of intrinsic safe models and some will be of

6-35

FSR on Expansion and Modernization of the MOIN Refinery Project

explosion proof types.

All temperature, pressure and differential pressure transmitters will be of smart types.

Differential pressure type flow meters are preferred in flow measurement. Mass flow

meters are preferred for the measurement of major materials at unit BL/plant boundary. Flow

rate measurement for high temperature and viscous fluid (temperature =200

) will use

wedge type flow meters. Flow rate measurement for medium and low temperature viscous

fluid (temperature < 200

) will use target flow transmitter. Flow rate measurement of steam

and fuel gas at the inlet of the unit and blower will use averaging pitot tube flow meter.

Level gauges will normally use differential pressure or flange type differential pressure

transmitters. For small range levels, electric external buoy or pneumatic external buoy level

gauges will be used.

Normally regulating valves to be used include cage type regulating valves, pneumatic

piston cutoff valve, pneumatic long travel actuator, and self powered regulating valve.

Regulating valves for high flow viscous oil fluid usually use eccentric rotary valves.

Thermocouples in heater tube wall will be of double edge models.

Online analyzers: Naphtha dry point analyzers, online pH meters and zirconia analyzers

for heater flue gas will be installed according to process requirements.

Safety detection instruments: Where flammable gas leakage is possible, e.g., blow down

points, compressor room and pump station, flammable gas detectors will be installed with

signals transmitted to CCR for display and alarm in FGDS.

Input safety barriers for temperature adjustment loops will use isolation types with

temperature transmitting functions.

In order to meet the high requirements of process for automatic control systems, world

advanced, proven and reliable DCS will be used in the unit.

SIS shall be product certified by corresponding international safety qualification

organizations. Safety rating of the systems selected shall not be lower than that of process

unit.

6.4.3.6

900 KTA Hydrocracking Unit

Most field instruments in the unit will be of intrinsic safe models and some will be of

explosion proof types.

All temperature, pressure and differential pressure transmitters will be of smart types.

Thermometers: Thermocouples will be armored single type with K graduation in line

with IEC. Reactor with be equipped with multiple point thermocouples. Surface temperature

measurement for furnace tube will use knife type devices. High temperature and high pressure

6-36

FSR on Expansion and Modernization of the MOIN Refinery Project

(over 1500#) will use special thermocouples with thermowells. Multiple point thermocouples

manufactured according to licensor requirements will be used for reactor beds.

Pressure and pressure differential switches shall use products of reliable technology.

Accuracy requirements for metering instruments: Grade 1.0-1.5 within unit, Grade

0.5-1.0 at unit BL and Grade 0.2 at plant BL. Volumetric flow meters will be used for major

liquid feeds and products at unit BL and mass flow meters for other fluids.

Level gauges: Transparent level glasses will be used. Central measurement will use

external buoy, DP and radar level gauges or level switches.

Analyzers: Online circulating hydrogen content analyzer and flammable gas and toxic

gas alarm. Online H

S content analyzer.

2

Actuators: Regulating valves will be equipped with pneumatic actuators.

Electric/pneumatic valve positioners will be used. Regulating valves will be used for high

temperature, HP, and high pressure drop locations of ANSI1500# and above.  Cutoff

valves/vent valves for automatic protection will be used in SIS.

Input safety barriers for temperature adjustment loops will use isolation types with

temperature transmitting functions.

In order to meet the high requirements of process for automatic control systems, world

advanced, proven and reliable DCS will be used in the unit.

SIS shall be product certified by corresponding international safety qualification

organizations. Safety rating of the systems selected shall not be lower than that of process

unit.

Design principle for F & G system: Separate from DCS and SIS and capable of

communication with DCS.

Safety barriers: Use isolation type safety barriers.

Scope of instruments and control system to be supplied with equipment packages.

Instruments for compressor package will be supplied with the equipment package.

6.4.3.7

150 KTA Isomerization Unit

Most field instruments in the unit will be of intrinsic safe models and some will be of

explosion proof types.

All temperature, pressure and differential pressure transmitters will be of smart types.

Heater will be equipped with zirconia oxygen analyzers.

Mainly pneumatic diaphragm type actuators will be used. Single or double seat

regulating valves shall be selected according to different process conditions.

6-37

FSR on Expansion and Modernization of the MOIN Refinery Project

Differential pressure type flow meters are preferred in flow measurement. Mass flow

meters are preferred for the measurement of major materials at unit BL/plant boundary. Flow

rate measurement for high temperature and viscous fluid (temperature =200

) will use

wedge type flow meters. Flow rate measurement for medium and low temperature viscous

fluid (temperature < 200

) will use target flow transmitter. Flow rate measurement of steam

and fuel gas at the inlet of the unit and blower will use averaging pitot tube flow meter.

Level gauges will normally use differential pressure or flange type differential pressure

transmitters. For small range levels, electric external buoy or pneumatic external buoy level

gauges will be used.

Thermocouples in heater tube wall will be of double edge models.

Online analyzers: Zirconia analyzers for heater flue gas will be used according to process

requirements.

Safety detection instruments: Where flammable gas leakage is possible, e.g., blow down

points, compressor room and pump station, flammable gas detectors will be installed with

signals transmitted to CCR for display and alarm in FGDS.

In order to meet the high requirements of process for automatic control systems, world

advanced, proven and reliable DCS will be used in the unit.

SIS shall be product certified by corresponding international safety qualification

organizations. Safety rating of the systems selected shall not be lower than that of process

unit.

6.4.3.8

25 KTA H

Production Unit

2

Most field instruments in the unit will be of intrinsic safe models and some will be of

explosion proof types.

All temperature, pressure and differential pressure transmitters will be of smart types.

Field pressure indication shall use flange type diaphragm pressure gauge. Pressure

measurement for remote display in CCR will use pressure transmitters. Pressure

measurements for fluids with suspended matter and solid particles or crystalline and viscous

fluids will use flange type remote pressure transmitters.

Metering of critical liquid materials at unit BL will use mass flow meters.

Large water pipes will use ultrasonic flow meters.

Common flow measurements will use standard throttling devices. Steam will be

measured by nozzles.

Large size control valves will be of butterfly types.

Level meters usually use double flange type remote transmitters or guided wave electric

6-38

FSR on Expansion and Modernization of the MOIN Refinery Project

radar level transmitters. Field level indication usually uses magnetic flap type level gauges or

quartz tube color level gauges. Level switches are normally of tuning fork or float types.

Major actuators used in the unit include pneumatic regulating valves for continuous

control and pneumatic valves for on/off control (including on/off pneumatic ball valves and

on/off pneumatic control gate valves). Pneumatic regulating valves usually use pneumatic

diaphragm actuators with valve positioners or electric transducers. Automatic interlock valves

use cylindrical O type ball valve. On/off pneumatic ball valves shall be equipped with

solenoid valves and limiting switches.

Online analyzers: Zirconia oxygen analyzers for oxygen content in heater flue gas will

be installed according to process requirements.

Safety detection instruments: Where flammable gas leakage is possible, e.g., blow down

points, compressor room and pump station, flammable gas detectors will be installed with

signals transmitted to CCR for display and alarm in FGDS.

Input safety barriers for temperature adjustment loops will use isolation types with

temperature transmitting functions.

In order to meet the high requirements of process for automatic control systems, world

advanced, proven and reliable DCS will be used in the unit.

SIS shall be product certified by corresponding international safety qualification

organizations. Safety rating of the systems selected shall not be lower than that of process

unit.

Instruments to be supplied with equipment packages.

Some equipment, e.g., blowers and heaters in the unit will be equipped with baffle valves.

Automatic controls will be equipped with proper actuators.

PSA supporting instruments will be supplied with equipment packages.

6.4.3.9

Sulfur Recovery Unit

Most field instruments in the unit will be of intrinsic safe models and some will be of

explosion proof types.

All temperature, pressure and differential pressure transmitters will be of smart types.

Local temperature measurement instrument will use double metal thermometers. Remote

temperature measurement element will use IEC thermometers and multi-point armored

thermocouples.

Temperature measurement in sulfur production furnace will use special online infrared

thermometers.

Differential pressure type flow meters are preferred in flow measurement. Mass flow

6-39

FSR on Expansion and Modernization of the MOIN Refinery Project

meters are preferred for the measurement of major materials at unit BL/plant boundary.

Local level indication will use level glasses. Remote level gauges will use buoy electric

level transmitters or single/double flange smart level transmitters.

Analyzers: H

S/SO

ratio analyzers and hydrogen concentration analyzers will be

2

2

installed according to process requirements.

Regulating valves will be of cylindrical butterfly or pneumatic diaphragm models. Cutoff

valves for interlock and automatic protection systems will use pneumatic cutoff valves or hard

seal pneumatic metal cutoff butterfly valves.

Input safety barriers for temperature adjustment loops will use isolation types with

temperature transmitting functions.

In order to meet the high requirements of process for automatic control systems, world

advanced, proven and reliable DCS will be used in the unit.

SIS shall be product certified by corresponding international safety qualification

organizations. Safety rating of the systems selected shall not be lower than that of process

unit.

Design principle for F & G system: Separate from DCS and SIS and capable of

communication with DCS.

Safety barriers: Use isolation type safety barriers.

Scope of instruments and control system to be supplied with equipment packages.

Instruments for compressor package will be supplied with the equipment package.

6.4.3.10

Dry Gas / LPG Scrubbing Unit

Most field instruments in the unit will be of intrinsic safe models and some will be of

explosion proof types.

All temperature, pressure and differential pressure transmitters will be of smart types.

Local temperature measurement instrument will use double metal thermometers. Remote

temperature measurement elements will use IEC thermometers and multi-point armored

thermocouples.

Temperature measurement in sulfur production furnace will use special online infrared

thermometers.

Differential pressure type flow meters are preferred in flow measurement. Mass flow

meters are preferred for the measurement of major materials at unit BL/plant boundary.

Local level indication will use level glasses. Remote level gauges will use buoy electric

level transmitters or single/double flange smart level transmitters.

6-40

FSR on Expansion and Modernization of the MOIN Refinery Project

Analyzers: H

S/SO

ratio analyzers and hydrogen concentration analyzers will be

2

2

installed according to process requirements.

Regulating valves will be of cylindrical butterfly or pneumatic diaphragm models. Cutoff

valves for interlock and automatic protection systems will use pneumatic cutoff valves or hard

seal pneumatic metal cutoff butterfly valves.

Input safety barriers for temperature adjustment loops will use isolation types with

temperature transmitting functions.

In order to meet the high requirements of process for automatic control systems, world

advanced, proven and reliable DCS will be used in the unit.

SIS shall be product certified by corresponding international safety qualification

organizations. Safety rating of the systems selected shall not be lower than that of process

unit.

Design principle for F & G system: Separate from DCS and SIS and capable of

communication with DCS.

Safety barriers: Use isolation type safety barriers.

6.4.4

Selection of major instruments and equipment

List of major instruments and equipment divided into domestic procurement and

offshore procurement are attached below.

The following illustrates selection and scope of supply for instruments and control

systems for grass root units. I/O points for DCS and SIS will be calculated with 15% margin.

A large DCS will be used with operation stations configured according to process unit

configuration to achieve process control of all units. A separate SIS will be configured

according to the requirements for unit interlock protection.

6.4.4.1

2,000 KTPA ADU and 1,500KTPA VDU

Table6.4-1 List of Major Instruments and Equipment

Item Description  Unit Quantity

I Thermometers

1  Armored thermocouples (with external thermowell)  Piece  240

2  Knife type armored thermocouples  Piece  60

3 Double metal thermometers Piece 50

II Flow meters

1 Throttling devices Set 75

2 Electromagnetic flow meters Set 2

3 Rotameters Set 28

6-41

FSR on Expansion and Modernization of the MOIN Refinery Project

Item Description  Unit Quantity

4 Double rotameters Set 7

5  Wedge type flow meters  Set  31

6  Mass flow meters  Set  5

7  Averaging pitot tube flow meters  Set  9

8  Target type flow meters  Set  28

9  Ultrasonic flow meters (mono channel)  Set  3

III Level gauges

1 Level glasses Set 37

2  Magnetic flap level meters  Set  15

3  Magnetic hysteresis retractable level transmitters  Set  6

4 Buoy level transmitters Set 16

5  Float level transmitters  Set  5

IV Actuators

1 Regulating valves Set 88

2  Eccentric rotary regulating valves  Set  65

3 Butterfly valves Set 13

4  T type regulating valves  Set  2

5  Pneumatic cutoff valve  Set  17

6 Self-powered regulating valves Set 7

7  Electric track ball valves  Set  2

8 Electric butterfly valves Set 2

9  Electric gate valves  Set  66

10  Smart valve positioners  Set  166

V Transmitters

1  Smart pressure transmitters  Set  80

2  Smart DP transmitters  Set  120

3  Smart single flange transmitters  Set  10

4  Smart double flange transmitters  Set  65

VI Analyzers

1  Online naphtha dry point analyzers  Set  1

2  Zirconia oxygen analyzers  Set  4

3 Online pH analyzers Set 3

4  Fuel gas density analyzers  Set  1

5  Kerosene distillation range analyzer  Set  1

6  Flammable gas detectors  Set  40

7  Toxic gas detectors  Set  8

VII DCS  Set 1

6-42

FSR on Expansion and Modernization of the MOIN Refinery Project

Item Description  Unit Quantity

VIII SIS  Set 1

IX FGDS  Set 1

X AMS Set 1

XI Miscellaneous instruments

1  Field rotating alarm lights  Set  20

2  Automatic flame endoscope  Set  2

3  Polling logging system  Set  1

4  Isolation and Flushing Unit  Set  1

5 Analytic cabin Set 2

6 Corrosion detection system Set 1

7  Isolating safety barriers  Set  750

8 Surge protectors Set 1000

9 Signal isolators Set 40

10 Local indicators  Set 20

11  Multiplex temperature collecting system  Set  13

6-43

FSR on Expansion and Modernization of the MOIN Refinery Project

6.4.4.2

700 KTPA Delayed Coking Unit

Table6.4-2 List of Major Instruments and Equipment

Item Description  Unit Quantity

I Thermometers

1 Double metal thermometers Piece 200

2 Thermocouples Piece 166

3  Armored surface thermocouples K type PN10  Piece  6

II Pressure gauges

1  SS pressure gauges  Set  221

2  Diaphragm type pressure gauges  Set  50

3  Micro pressure gauges  Set  20

4 Pressure switches  Set 8

III Level gauges

1  Level glasses for viscous fluids  Set  7

2 Level glasses  Set 65

3  Electric external buoy level/interface transmitters  Set  15

4  Electric float level transmitters  Set  13

5 Radar level gauges  Set 10

6 Radioactive level gauges  Set 1

7 Level switches  Set 2

IV Flow meters

1 Ultrasonic flow meters  Set 4

2  Thermal conductor flow meters  Set  4

3 Throttling devices  Set 80

4  Mass flow meters    4

V Actuators

1 Regulating valves  Set 115

2 Cutoff ball valves  Set 8

3  Long travel actuators  Set  16

4  Smart electric/pneumatic positioners

Electric/pneumatic transducers  Set 133

5 Solenoid valves  Set 32

6 Self-powered regulating valves  Set 9

7 Butterfly valves  Set 5

VI Transmitters

1  Smart temperature transmitters  Set  40

2  Smart pressure transmitters  Set  50

6-44

FSR on Expansion and Modernization of the MOIN Refinery Project

Item Description  Unit Quantity

3  Smart DP transmitters  Set  80

4  Smart double flange transmitters  Set  30

5  Smart micro DP transmitters  Set  14

VII Analyzers

1  Flammable gas content alarms  Set  30

2 H2S content alarms  Set 5

3  Zirconia oxygen analyzers  Set  2

VIII DCS  Set 1

IX SIS  Set 1

X FGDS  Set 1

XI AMS  Set 1

XII Miscellaneous instruments

1  Polling logging system  Set  1

2  Isolation and Flushing Unit  Set  1

3 Analytic cabin  Set 1

4  Isolating safety barriers  Set  626

5 Surge protectors  Set 700

6 Signal isolators  Set 30

6-45

FSR on Expansion and Modernization of the MOIN Refinery Project

6.4.4.3

500 KTA Continuous Catalytic Reforming Unit

Table6.4-3 List of Major Instruments and Equipment

Item Description  Unit Quantity

I Thermometers

1 Double metal thermometers  Set 100

2  Internal leakage free armored thermocouples with SS

thermowells  Piece 165

3  Internal leakage free armored thermocouples with Monel

thermowells  Piece 10

4 Surface thermocouples  Piece 20

5  Knife type furnace tube surface thermocouples  Piece  20

6  Multi-point armored thermocouples, 7 points  Set  2

7  Multi-point flexible thermocouples, 16 points  Set  1

8  Multi-point temperature collection unit, 8 points  Set  20

II Pressure gauges

1  SS pressure gauges  Piece  200

III Flow meters

1 Throttling devices  Set 47

2 Venturi tubes  Set 5

3 Rotameters  Set 12

4  Mass flow meters  Set  4

5  Thermal mass flow meters  Set  1

6 Ultrasonic flow meters  Set 3

7  Internal orifice + Transmitters

ANSI 150lb  Set 1

ANSI 300lb  Set 1

8  Target type flow meters  Set  4

IV Level gauges

1 Level glasses  Set 42

2 Buoy level transmitters  Set 5

3  Capacitor type level switches  Set  1

4  Nuclear level switches  Set  4

5  Nuclear level transmitters  Set  5

6 Radar level transmitters  Set 1

V Smart transmitters

1 Pressure transmitters  Set 50

2 DP transmitters  Set 140

6-46

FSR on Expansion and Modernization of the MOIN Refinery Project

Item Description  Unit Quantity

3  Double flange level transmitters  Set  4

VI Actuators

1  Pneumatic plunger type regulating valves

(

1

)

ANSI 150lb

Carbon steel  Set 18

Stainless steel  Set 3

(

2

)

ANSI 300lb

Carbon steel  Set 14

Stainless steel  Set 7

Chromium-molybdenum steel  Set 6

(

3

)

ANSI 600lb

Carbon steel  Set 4

Stainless steel  Set 7

2  Pneumatic V-notched ball valve

ANSI 300lb

,

Stainless steel  Set  3

3  Pneumatic eccentric rotary valves

(

)

1

ANSI 150lb  Set 5

(

)

2

ANSI 300lb  Set 8

4  Pneumatic eccentric butterfly valves

ANSI 150lb  Set 9

5  Smart valve positioners, electric/pneumatic transducers Set  84

6  Electric gate valves  Set  24

7  Pneumatic on/off cutoff valves

Solenoid valves

(

1

)

Pneumatic on/off ball valves

ANSI 150lb  Set 14

ANSI 300lb  Set 13

ANSI 600lb  Set 3

(

2

)

Pneumatic on/off plunger valves

ANSI 150lb  Set 9

ANSI 300lb  Set 12

(

)

3

Eccentric rotary valves  Set  5

(

)

4

On/off V-notched ball valves

,

ANSI 300lb

Stainless steel  Set  13

(

)

5

On/off eccentric butterfly valves

ANSI 150lb  Set 5

6-47

FSR on Expansion and Modernization of the MOIN Refinery Project

Item Description  Unit Quantity

8  Electric on/off butterfly valves    35

9 Self-powered regulating valves   10

VII Flame detection

Chamber flame video supervision system

Totally 18 vediocams  Set 1

VIII Analyzers

1  Online zirconia oxygen content analyzers  Set  8

2  Online H2 content analyzers  Set  1

3  Online H2 content analyzers (Double sensor)  Set  1

4  Online trace water analyzers  Set  1

5  Online near infrared RON analyzers  Set  1

6  Online nitrogen/hydrocarbon/oxygen content analyzers Set  1

7  Gas density analyzers  Set  1

8  Flue gas composition analyzers  Set  1

9  Field flammable gas detection and alarm instruments

(

1

)

Flammable gas detectors (hydrocarbon)  Set  30

(

2

)

Flammable gas detectors (H2)  Set  6

(

3

)

Portable flammable gas alarms  Set  2

(

4

)

Field rotating alarm lights  Set  10

(

)

5

Sirens  Set 10

IX Control system

1 DCS  Set 1

2 SIS  Set 1

3 CCS  Set 1

4 FGDS  Set 1

5  Catalyst and regeneration control system  Set  1

6 AMS  Set 1

X Miscellaneous instruments

1  Explosion proof field current indicators  Set  20

2 Analytic cabin  Set 2

3 WRS  Set 1

Polling points: 30

4  Isolating safety barriers  Set  700

5 Surge protectors  Set 1000

6 Signal isolators  Set 60

6-48

FSR on Expansion and Modernization of the MOIN Refinery Project

6.4.4.4

1,300KTPA Diesel Hydrofining Unit

Table6.4-4 List of Major Instruments and Equipment

Item Description  Unit Quantity

I Thermometers

1 Double metal thermometers  Set 25

2 Normal armoured thermocouples  Set 90

3  Surface thermocouples (heaters)  Set  16

4  Reactor HP multi-point flexible thermocouples  Set  3 Set

(18 points)

5  Reactor armored surface thermocouples  Set  20

II Pressure gauges

1  SS pressure gauges  Set  90

2 Capsule pressure gauges  Set 12

III Flow meters

1 Throttling devices  Set 40

2 Rotameters  Set 2

3  Ultrasonic or vortex flow meters  Set  4

4  Mass flow meters  Set  2

5  Annubar flow meters  Set  2

6  Target type flow meters  Set  6

IV Level gauges

1 Level glasses  Set 20

2  Electric buoy level gauges  Set  6

3  Magnetic flap level meters (field + remote)  Set  10

4 Radar level gauges  Set 6

V Smart transmitters

1  Smart pressure transmitters  Set  30

2  Smart DP transmitters (with 3-valve manifold)  Set  60

4  Smart single flange DP transmitters  Set  3

5  Smart double flange DP transmitters  Set  10

VI Regulating valves

1  Pneumatic diaphragm regulating valves  Set  50

2 Self-powered regulating valves  Set 2

3  Explosion proof T type solenoid valves  Set  5

4  Long travel actuators  Set  3

6-49

FSR on Expansion and Modernization of the MOIN Refinery Project

Item Description  Unit Quantity

5  Pneumatic cutoff gate (ball) valves  Set  40

6  Electric fire proof cutoff gate (ball) valves  Set  5

7 Electric/pneumatic transducers  Set 4

8  Smart valve positioner  Set  50

VII Online analyzers

1 Zirconia analyzers  Set 2

2 Hydrogen content analyzers  Set 1

VIII Safety detection instruments

1  Flammable gas detection transmitters  Set  20

2  H2S gas detection transmitters  Set  15

3  H2 gas detection transmitters  Set  10

4  Portable flammable gas, H2S and H2 detectors  Set  3

5  Explosion proof loudspeakers  Set  6

6  Explosion proof lights  Set  6

IX DCS  Set 1

X SIS  Set 1

XI FGDS  Set 1

XII AMS  Set 1

XIII Miscellaneous instruments

1  Production safety inspection system  Set  1

2  Safety barrier cabinets and terminal cabinets  Set  3

3  Isolating safety barriers  Set  400

4 Surge protectors  Set 700

5 Signal isolators  Set 30

6  Explosion proof field current indicators  Set  5

6-50

FSR on Expansion and Modernization of the MOIN Refinery Project

6.4.4.5

550 KTA Naphtha Hydrotreating Unit

Table6.4-5 List of Major Instruments and Equipment

Item Description  Unit Quantity

I Thermometers

1 Double metal thermometers  Set 30

2  Common armored thermocouples with SS thermowells Piece  92

3  Reactor HP multi-point flexible thermocouples, 40 points Set  3

4  Surface thermocouples (for heater)  Piece  10

5  Reactor armored surface thermocouples  Piece  10

II Pressure gauges

1  SS pressure gauges  Piece  105

III Flow meters

1 Throttling devices  Set 45

2 Rotameters  Set 6

3  Mass flow meters  Set  3

4 Ultrasonic flow meters  Set 4

5  Averaging pitot tube flow meters  Set  3

6  Target type flow meters  Set  6

IV Level gauges

1 Level glasses PN5.0  Set 15

2 Buoy level transmitters  Set 6

3  Magnetic flap level meters (field + remote)  Set  10

4 Radar level transmitters  Set 1

V Smart transmitters

1 Pressure transmitters  Set 30

2 DP transmitters  Set 66

3  Single flange level transmitters  Set  3

4  Double flange level transmitters  Set  10

VI Regulating valves

1  Pneumatic plunger type regulating valves  Set  57

2  Smart valve positioner  Set  57

VII  Pneumatic on/off cutoff valves (with solenoid valves)

ON/OFF ball valves  Set 46

VIII  Electric fire proof cutoff ball valves  Set  8

IX  Self-powered pressure regulating valves  Set  6

X  Field flammable gas detection and alarm instruments

6-51

FSR on Expansion and Modernization of the MOIN Refinery Project

Item Description  Unit Quantity

1  Flammable gas detectors (H2S)  Set  15

2  Flammable gas detectors (H2)  Set  10

3  Flammable gas detectors (hydrocarbon)  Set  5

4  Portable flammable gas alarms (flammables, H2S and H2) Set  3

5  Field rotating alarm lights  Set  7

6 Sirens  Set 7

7  Ultraviolet flame detectors  Set  28

XI Online analyzers

1  Online zirconia oxygen content analyzers  Set  3

XII DCS  Set 1

XIII SIS  Set 1

XIV CCS  Set 1

XV AMS  Set 1

XVI Miscellaneous instruments

1 WRS  Set 1

2  Explosion proof field current indicators  Set  12

3  Isolating safety barriers  Set  560

4 Surge protectors  Set 850

5 Signal isolators  Set 30

6-52

FSR on Expansion and Modernization of the MOIN Refinery Project

6.4.4.6

900 KTA Hydrocracking Unit

Table6.4-6 List of Major Instruments and Equipment

Item Description  Unit Quantity

I Thermometers

1 Double metal thermometers Piece 50

2 Armored thermocouples Piece 93

3  Furnace tube surface thermocouples  Piece  27

4  HP armored thermocouples  Piece  72

5  HP multi-point thermocouples (3 points)  Piece  12

6  HP multi-point thermocouples (22 points)  Piece  4

7 Surface thermocouples Piece 104

II Pressure gauges

1  Common pressure gauges  Piece  114

2 Capsule pressure gauges Piece 6

3  Vibration proof pressure gauges  Piece  50

4  Diaphragm pressure gauges  Piece  15

III Flow meters

1  LP flanged throttling devices  Set  74

2  HP flanged throttling devices  Set  30

3 Vortex flow meter Set 10

4 Electromagnetic flow meters Set 2

5 Integrated small orifice Set 8

6  Mass flow meters  Set  6

7  Annubar flow meters  Set  4

IV Level gauges

1  Double color level glasses  Set  60

2  Magnetic flap level meters  Set  8

3  LP external buoy level transmitters  Set  30

4  HP external buoy level transmitters  Set  14

5  Magnetic retractable level gauges  Set  4

V Smart transmitters

1  Smart pressure and DP transmitters  Set  170

2  Smart double flange DP transmitters  Set  10

3  Smart high static pressure double flange DP transmitters  Set  18

4 Safety barriers Set 950

5 Surge protectors Set 1300

6-53

FSR on Expansion and Modernization of the MOIN Refinery Project

Item Description  Unit Quantity

VI Safety instruments

1 FGDS Points 70

VII Actuators

1 Regulating valves Set 70

2  Eccentric rotary valves  Set  17

3  HP diaphragm regulating valves  Set  30

4  HP cutoff valves  Set  10

5 Self-powered regulating valves Set 10

6  LP gate valves  Set  10

IX Analyzers

1  Gas density analyzers  Set  1

2  Zirconia flue gas oxygen content analyzers  Set  2

X SIS Set 1

XI DCS Set 1

XII CCS  Set 1

XIV FGDS  Set 1

XV Miscellaneous instruments  Set 8

1  Safety barriers, surge protectors and terminal cabinets  Set  8

2 Power supply cabinets Set 1

3 WRS Set 1

6-54

FSR on Expansion and Modernization of the MOIN Refinery Project

6.4.4.7

150 KTA Isomerization Unit

Table6.4-7 List of Major Instruments and Equipment

Item Description  Unit Quantity

I Thermometers

1 Double metal thermometers Set 30

2 LP single/double thermocouples Piece 40

II Pressure gauges

1  SS pressure gauges  Set  40

III Flow meters

Mass flow meters  Set  2

Electromagnetic flow meters Set 2

Metal Rotameters Set 1

Throttling devices Set 25

IV Level gauges

Double color level glasses  Set  20

Explosion proof level switches  Set  5

Electric external buoy level (interface) transmitters  Set  10

V Smart transmitters

Smart temperature transmitters  Set  5

Smart pressure transmitters  Set  20

Smart DP transmitters  Set  25

Smart double flange DP transmitters  Set  2

VI Actuators

Pneumatic regulating valves Set 30

Pneumatic long travel actuators  Set  1

Electric/pneumatic valve positioners  Set  30

VII  Flammable gas detectors and alarms  Set  10

VIII Analyzers

Online zirconia analyzers    1

IX DCS  Set 1

X SIS  Set 1

XI FGDS  Set 1

XII AMS  Set 1

XIII Miscellaneous instruments

1  Production safety inspection system  Set  1

3  Isolating safety barriers  Set  150

6-55

FSR on Expansion and Modernization of the MOIN Refinery Project

Item Description  Unit Quantity

4 Surge protectors Set 400

5 Signal isolators Set 20

6-56

FSR on Expansion and Modernization of the MOIN Refinery Project

6.4.4.8

25 KTA H

Production Unit

2

Table6.4-8 List of Major Instruments and Equipment

Item Description  Unit Quantity

I Thermometers

1 Double metal thermometers Piece 20

2  Internal leakage free armored RTD with SS thermowells  Piece  24

3  Internal leakage free armored thermocouples with SS thermowells Piece  101

II Pressure gauges

1  SS pressure gauges  Set  50

2  Stainless steel DP gauges  Set  12

III Flow meters

1 Throttling devices  Set 33

2 Rotameters  Set 7

3  Mass flow meters  Set  2

4 Ultrasonic flow meters  Set 1

IV Level gauges

1 Level glasses  Set 10

2  Magnetic flap level meters  Set  7

3 Level switches  Set 4

4 Radar level gauges  Set 4

V Smart transmitters

1  Smart pressure transmitters  Set  102

2  Smart DP transmitters  Set  99

VI  Control valves (with smart positioners)

1 Plunger valves  Set 79

2 Butterfly valves  Set 7

3 Gate valves  Set 3

4 Angle control valves  Set 8

5  Eccentric butterfly valves  Set  2

VII  Pneumatic cutoff valves (with valve position switches)

1 Ball valves  Set 10

2  Eccentric butterfly valves  Set  6

VIII Online analyzers

1 pH analyzers  Set 1

2  DMW conductivity analyzers  Set  1

3 Zirconia analyzers  Set 2

6-57

FSR on Expansion and Modernization of the MOIN Refinery Project

Item Description  Unit Quantity

4  CO concentration analyzer  Set  1

5  H2 concentration analyzer  Set  4

IX  Field part of FGDS

1  Flammable gas detectors (with acoustic and visual alarms)  Set  56

2  Manual alarm push buttons  Set  25

3  Rotating alarm lights  Set  25

4 Sirens  Set 25

X Flame detectors  Set 5

XI DCS  Set 1

XII SIS  Set 1

XIII FGDS  Set 1

XIV AMS  Set 1

XV Miscellaneous instruments

1  Temperature transmitting isolation barriers  Set  125

2  Isolating safety barriers  Set  601

3 Surge protectors  Set 812

4 Signal isolators  Set 12

5  Production safety inspection system  Set  1

6-58

FSR on Expansion and Modernization of the MOIN Refinery Project

6.4.4.9

900 KTA Hydrocracking

Table6.4-9 List of Major Instruments and Equipment

Item Description  Unit Quantity

I Thermometers

1  Armored thermocouples (with external thermowell)  Piece  50

2  Special thermocouples for sulfur reactor  Piece  12

3 Double metal thermometers Piece 40

4 Infrared thermometers  Set 5

5 Multi-point armored thermocouples  Set 10

II Flow meters

1 Throttling devices  Set 40

2 Electromagnetic flow meters  Set 4

3 Rotameters  Set 4

4  Wedge type flow meters  Set  4

5  Thermal gas mass flow meters  Set  9

6  Ultrasonic flow meters (mono channel)  Set  10

7  Averaging pitot tube flow meters  Set  3

III Level gauges

1 Level glasses  Set 40

2  Magnetic flap level meters  Set  10

3 Buoy level transmitters  Set 14

IV Gas analyzers

1  Flammable gas detectors  Set  15

2  Toxic gas detectors

(

H2S

)

Set 12

V Actuators

1 Regulating valves  Set 45

2  Smart valve positioner and transducers  Set  45

3  Pneumatic cutoff valves with solenoid valves  Set  30

VI Smart transmitters

1  Smart pressure transmitters  Set  50

2  Smart DP transmitters  Set  20

3  Smart single flange transmitters  Set  4

4  Smart double flange transmitters  Set  10

VII  Analyzers

1 Online pH analyzer  Set 2

2 Zirconia analyzers  Set 3

6-59

FSR on Expansion and Modernization of the MOIN Refinery Project

Item Description  Unit Quantity

3 H2 analyzers  Set 1

4 SO2 analyzers  Set 1

5  H2S/SO2 ratio analyzers  Set  2

VIII DCS  Set 1

IX SIS  Set 1

X FGDS  Set 1

XI AMS  Set 1

XII Miscellaneous instruments

1  Field rotating alarm lights  Set  20

2  Automatic flame endoscope  Set  2

3  Polling logging system  Set  1

4 Analytic cabin  Set 1

5  Multiplex temperature collecting system  Set  2

6  Isolating safety barriers  Set  570

7 Surge protectors  Set 800

8 Signal isolators  Set 20

6-60

FSR on Expansion and Modernization of the MOIN Refinery Project

6.4.4.10

Dry GAS / LPG Treatment Unit

Table6.4-10 List of Major Instruments and Equipment

Item Description  Unit Quantity

I Thermometers

1  Multi-point armored thermocouples (with integrated temperature

transmitters)  Set 3

2  Integrated temperature transmitters  Set  50

II Flow meters

1 Throttling devices Set 40

2 Electromagnetic flow meters Set 2

3 Rotameters Set 3

4  Mass flow meters  Set  5

5 Vortex flow meter   10

III Level gauges

1 Level glasses Set 30

2 Buoy level transmitters Set 10

3 Float controllers Set 5

4 Radar level gauges Set 4

IV Gas analyzers

1  Flammable gas detectors  Set  15

2  Toxic gas detectors  Set  10

V Actuators

1 Regulating valves Set 60

2  Smart valve positioners  Set  60

VI Smart transmitters

1  Smart pressure transmitters  Set  40

2  Smart DP transmitters  Set  60

3  Smart double flange transmitters  Set  15

VII DCS  Set 1

VIII AMS  Set 1

IX FGDS  Set 1

X Miscellaneous instruments

1  Polling logging system  Set  1

2  Field rotating alarm lights  Set  20

3  Isolating safety barriers  Set  220

4 Surge protectors Set 350

6-61

FSR on Expansion and Modernization of the MOIN Refinery Project

5  Isolation liquid automatic flushing system  Set  1

6-62

FSR on Expansion and Modernization of the MOIN Refinery Project

6.5 Automatic Control Program for Logistics System

6.5.1

Tank Farm Monitoring and Management

6.5.1.1

Tank farm monitoring and management consists of the following targets:

(1)

Monitoring of process parameters including tank level, temperature and pressure;

High precision tank detection instruments will be used, e.g., radar, servo, static pressure

level gauges and other instruments. Average thermometers, pressure transmitters and level

switches will be installed according to practical needs. All field signals will be transmitted to

remote I/O stations for the tank farm, from where they are transmitted via fiber optic into

DCS in CCR for central display and control.

Oil tank level will be equipped with tank side indicators without any other field

instruments.

(2)

Tank inventory calculation function;

(3)

Process parameter over limit alarm;

(4)

Oil-water interface detection and automatic water cutting (for crude storage tank);

(5)

Tank oil inventory calculation;

(6)

Automatic switching between tanks;

Pump suction and discharge pipelines will be equipped with pneumatic wedge type gate

valves with manual operation and field explosion proof control box. Valve operation could be

done on site or in control room with valve status display in CCR.

(7)

Flammable gas detection and alarm

6.5.2

Selection of Major Instruments

(1)

Level, interface and density for final products including diesel and kerosene will be

measured by servo level gauges. Tank temperature will be measured by averaging

thermometers with tank side indicators.

(2)

Crude tank and intermediate product tank levels will be measured by radar level

gauges with tank side indicators.

(3)

LPG tank level will be measured by servo level gauges and tank temperature will be

measured by averaging thermometers with tank side indicators.

(4)

Tank temperature will be measured by Pt100 platinum RTD.

(5)

Cutoff valves will be pneumatic wedge type gate valve with manual operation.

6-63

FSR on Expansion and Modernization of the MOIN Refinery Project

6.5.3

Major Instruments and Equipment

6.5.3.1

Crude Storage Tank Farm

Table6.5-1 List of Major Instruments and Equipment

Item Description  Unit Quantity Remarks

1 Platinum RTD  Set 6

2 Smart level gauges Set 6

3 Level switches  Set 12

4  Pneumatic cutoff valves  Set  12

5  Flammable gas alarms  Set  24

6.5.3.2

Intermediate Product Storage Tank Farm

Table6.5-2 List of Major Instruments and Equipment

Item Description  Unit Quantity Remarks

1 Platinum RTD  Set 24

2 Smart level gauges Set 24

3 Level switches  Set 48

4  Pneumatic cutoff valve  Set  48

5  Flammable gas alarms  Set  60

6.5.3.3

Oil Product Storage Tank Farm (kerosene and diesel)

Table6.5-3 List of Major Instruments and Equipment

Item Description  Unit Quantity Remarks

1 Platinum RTD  Set 23

2 Smart level gauges Set 23

3 Level switches  Set 46

4  Pneumatic cutoff valve  Set  46

5  Flammable gas alarms  Set  60

6.5.3.4

Heavy Oil Storage Tank Farm

Table6.5-4 List of Major Instruments and Equipment

Item Description  Unit Quantity Remarks

1 Platinum RTD  Set 4

2 Smart level gauges Set 4

3 Level switches  Set 8

4  Pneumatic cutoff valve  Set  8

6-64

FSR on Expansion and Modernization of the MOIN Refinery Project

5  Flammable gas alarms  Set  15

6.5.3.5

LPG Storage Tank Farm

Table6.5-5 List of Major Instruments and Equipment

Item Description  Unit Quantity Remarks

1 Platinum RTD  Set 15

2 Smart level gauges Set 15

3 Level switches  Set 30

4  Smart pressure transmitters  Set  15

5  Pneumatic cutoff valve  Set  30

6  Flammable gas alarms  Set  20

6.6 Automatic Control Program for Utilities and Auxiliary Production

Facilities

6.6.1

Control Level and Major Control Program

Utilities include air compression station, nitrogen station, fire water pump station, water

feed system, circulating water system, water purification plant, waste water treatment plant,

DMW plant, plant water supply and drainage pipe system, and water pollution control and

prevention system (including clean rainwater collection system, polluted rainwater collection

system and water pool and emergency polluted water collection system and water pool), and

pumping system.

Large utility facilities, e.g., air separation and boilers shall be equipped with local control

room (LCR) with separate DCS and PLC control systems capable of communicating with

CCR.

Other utility facilities may use local panels (LP) with critical process parameters and

alarm signals connected to CCR.

6.6.2

Instrument Selection

Identical with process units.

6.6.3

Major Instruments and Equipment

Table6.6-1 List of Major Instruments and Equipment for Boilers

Item Description  Unit Quantity Remarks

1 Transmitters  Set 260

2 Pneumatic regulating valves Set 95

6-65

FSR on Expansion and Modernization of the MOIN Refinery Project

3  Online conductivity analyzers  Set  2

4  Online conductivity analyzers  Set

2

5 Dissolved oxygen analyzers Set 2

Table6.6-2 List of Major Instruments and Equipment for Utilities

Item Description  Unit  Quantity Remarks

1  Pressure and level transmitters  Set  95

2 Flow transmitters  Set 40

3 Regulating valves  Set 30

4  Online pH value analyzer  Set  2

5  Online COD analyzer  Set  2

6  Online analyzer for oil content in water  Set  2

7  Online dissolved oxygen analyzers  Set  3

8  Online dissolved oxygen analyzers  Set  3

6.7 Central Control Room

6.7.1

General

This section covers study on control rooms for grass root units and revamp units in the

Project.

CCR is a critical plant wide operation area for the control and management of all grass

root production units, logistic facilities including feed stock tank farm and intermediate feed

tank farm as well as utilities.

DCS will be installed in CCR for data acquisition, information processing, process

control, input/output material metering, alarm, and safety interlocks for all process units,

logistic facilities and utilities.

6.7.2

Specific Configuration Program

Because existing control room could not meet the requirements of the new refineries, a

new CCR will be built to meet the requirements of refineries, logistic system and water

supply and drainage system.

The new CCR will be built in non explosion hazard area with explosion proof structures.

Each control room will be equipped with DCS operation room, cabinet room, engineer room,

instrument reference room, dispatching/communication room, shift room, administration

office, meeting room, changing room, lounge, training room, workshop, toilets, UPS room,

and air conditioner room.

6-66

FSR on Expansion and Modernization of the MOIN Refinery Project

Table6.7-1 Building Area, Control Range and Configuration of CCR

Description  Building Area

(m2)   Control Range  Configuration

New refineries  32 operation stations

New logistic system  2operation stations

Central control room  2000

Water supply and drainage

system  1 operation station

6-67

FSR on Expansion and Modernization of the MOIN Refinery Project

6.8 Major Codes and Standards Referenced in Design

Name and number of major Codes and standards referenced in design are shown below:

RP 30-6      Design of Protective Instrument Systems (IEC 61508)

ISA    Instrument Society of America

ISA S5.1 (1984)   Instrumentation Symbols and Identification

ISA S50-1 (1982)  Compatibility of Analogue Signals for Electronic Industrial Process

Instruments

ISA S75-01 (1995)  Flow Equations for Sizing Control Valves

ISA RP 55.1    Hardware Testing of Digital Process Computers

API    American Petroleum Institute

API RP500   Manual on Installation of Refinery Instruments and Control

Systems

API RP551 (1993)  Process Measurement and Instrumentation

API RP554 (1995)  Process Instrumentation and Control

API RP555 (1995)  Process Analyzers

API 670 (2000)    Vibration,  Axial  Position  and Bearing Temperature Monitoring

Systems

ANSI /NFPA    American  National  Standards Institute / National Fire Protection

Association 70 National Electric Code (NEC)

IEC 60381      Analogue Signals for Process Control Systems

Part 1 (1982)    Direct Current Signals

Part 2 (1978)    Direct Voltage Signals

IEC 60382 (1991)  Analogue Pneumatics Signals for Process Control Systems

IEC 60534 (1987)  Industrial – Process Control Valves

IEC 60751 (1995)  Industrial Platinum Resistance Sensors

IEC 61508

Part 1 (1999)    Functional  Safety  Of Electrical/Electronic/ Programmable

Electronic Safety-Related System: General requirements

Part 2 (2000)    Requirements  for  electrical/ Electronic/Programmable/Electronic

Safety related systems

Part 3 (1999)    Software Requirements

6-68

FSR on Expansion and Modernization of the MOIN Refinery Project

Part 4 (1999)    Definitions and Abbreviations

Part 5 (1999)    Example of Methods for the Determination of Safety Integration

Levels

Part 6 (2000)    Guideline on the Application of IEC 61508-2 and IEC 61508-3

Part 7 (2000)    Overview of Techniques and Measures

IEC 61000-4 (2001)  Electromagnetic  Compatibility (EMC) – Part 4: Testing and

Measurement Techniques

NFPA 70   National Electrical Code and National Fire Protection Agency

Standards

ASME B40.100 (1998)  Pressure Gauges and Gauge Attachments

ANSI/FCI 70-2(1991)  Quality Control Standard for Control Valve Seat Leakage

ASME B16. 10(2000)  Face To Face Dimensions For Ferrous Valves

AGA          Measurement of Gas by Multipath Ultrasonic Meters:

Transmission Measurements Committee Report 9 (1998)

ISO 5167 (1980)    Measurement of Flow of Fluids by Means of Orifice Plates,

Flow Nozzles and Venturi Tubes Inserted in Circular Conduits Running Full

ISO 5167-1 (1998)    Specifications  for  Square Edged Orifice Plates, Nozzles and

Venturi Tubes

AGA            Orifice Metering of Natural Gas Report 3 (1990)

IEEE-802.3 (2000)    Information Processing Systems – Local Area Networks

DIN V 19250 (1994)   Measurement  and  Control Fundamental Safety Aspects for

Measurement and Control Protective Equipment.

Stipulations on the Preparation of Feasibility Study Report for Refinery Projects with

Overseas Investment.

6-69